## 119_16
S&C Power Fuses - Types SMD-2B and SMD-3 (69 kV) | [9 empty] | S&C Power Fuses - Types SMD-2B and SMD-3 (69 kV) | [9 empty] | S&C Power Fuses - Types SMD-2B and SMD-3 (69 kV) | [9 empty] | S&C Power Fuses - Types SMD-2B and SMD-3 (69 kV)
Slow Speed (TCC 119-1-6) | [9 empty] | Slow Speed (TCC 119-1-6) | [9 empty] | Slow Speed (TCC 119-1-6) | [9 empty] | Slow Speed (TCC 119-1-6)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E |  | 2-200E |  | 2-250E |  | 2-300E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
25007.4 | 0.030102 | 25007.4 | 0.030102 | 25007.4 | 0.030102 | 25007.4 | 0.030223 | 25007.4 | 0.030223 | 25007.4 | 0.030313 | 25007.4 | 0.030404 | 25007.4 | 0.030618 | 25007.4 | 0.030988 | 24787.8 | 0.032442 | 24787.8 | 0.033442 | 24816.2 | 0.034021 | 24787.8 | 0.03463 | 24787.8 | 0.03527 | 24773.6 | 0.038875 | 24773.6 | 0.039821 | 24787.8 | 0.046211 | 24787.8 | 0.060407
22469.7 | 0.030679 | 22741 | 0.030679 | 22946.6 | 0.030618 | 23410.2 | 0.030526 | 22877.9 | 0.030679 | 22201.7 | 0.030988 | 22923.7 | 0.030895 | 22900.8 | 0.031174 | 23107.8 | 0.031487 | 21978.4 | 0.033403 | 21890.4 | 0.034452 | 22539.4 | 0.034829 | 22733.9 | 0.035717 | 22308.1 | 0.037348 | 23101.4 | 0.04072 | 22257.1 | 0.043391 | 22890.7 | 0.050672 | 23181 | 0.065785
21034.6 | 0.031081 | 21309.9 | 0.030988 | 21524 | 0.030988 | 21980.8 | 0.030895 | 21438.1 | 0.031081 | 20762.9 | 0.031393 | 21502.5 | 0.031299 | 21459.6 | 0.031677 | 21675.2 | 0.031995 | 17831.7 | 0.035371 | 18234.6 | 0.036503 | 19365 | 0.036838 | 19013.2 | 0.038653 | 19199.3 | 0.040813 | 20742.9 | 0.044016 | 19122.4 | 0.050124 | 20238.2 | 0.058301 | 20471.4 | 0.077531
19612.6 | 0.031487 | 19889.1 | 0.031393 | 20088.9 | 0.031393 | 20556.3 | 0.031299 | 20008.8 | 0.031487 | 19339.9 | 0.031899 | 20068.9 | 0.031804 | 20028.8 | 0.032188 | 20250.3 | 0.032609 | 14650.9 | 0.037843 | 14870.7 | 0.039684 | 16410.5 | 0.039458 | 15792.6 | 0.04195 | 16752.4 | 0.044421 | 18286.9 | 0.048404 | 16675.8 | 0.057769 | 17618.5 | 0.069661 | 17841.9 | 0.094081
18177.2 | 0.031899 | 18451.9 | 0.031899 | 18656 | 0.031804 | 19128.3 | 0.031677 | 18581.6 | 0.031995 | 17906.6 | 0.032382 | 18637.4 | 0.032285 | 18600.1 | 0.032707 | 18824.7 | 0.033201 | 12162.2 | 0.040696 | 11805.3 | 0.044168 | 13677.6 | 0.043045 | 13291.5 | 0.046556 | 14634.1 | 0.048905 | 16326.1 | 0.053381 | 14777.3 | 0.066201 | 15417.2 | 0.083186 | 15693.4 | 0.11403
16746.2 | 0.032382 | 17033.3 | 0.032285 | 17221.7 | 0.032285 | 17693 | 0.032188 | 17152.9 | 0.032511 | 16480.4 | 0.033003 | 17204.5 | 0.032904 | 17170.1 | 0.033301 | 17394.8 | 0.034008 | 10265.4 | 0.043966 | 9929.98 | 0.048682 | 11295.9 | 0.04788 | 11399.9 | 0.051668 | 12267.2 | 0.056559 | 13954.6 | 0.061629 | 12960.6 | 0.078155 | 13669.8 | 0.098828 | 13882.9 | 0.13941
15320.2 | 0.033003 | 15598.4 | 0.032904 | 15802.5 | 0.032805 | 16267.5 | 0.032707 | 15723.7 | 0.033102 | 15046.9 | 0.033602 | 15770.9 | 0.033501 | 15739.4 | 0.03411 | 15961.3 | 0.034799 | 8521.7 | 0.048487 | 8262.14 | 0.05531 | 9693.93 | 0.052925 | 9441.84 | 0.060269 | 10551.6 | 0.065672 | 11893.5 | 0.072675 | 11690.9 | 0.089408 | 12037.5 | 0.12116 | 12408.5 | 0.1682
13890 | 0.033602 | 14170.6 | 0.033501 | 14370.4 | 0.033401 | 14837.7 | 0.033301 | 14298.7 | 0.033703 | 13628.6 | 0.034315 | 14341.7 | 0.034212 | 14313 | 0.034904 | 14529.3 | 0.035787 | 6969.59 | 0.054994 | 7135.21 | 0.062913 | 8468.17 | 0.059006 | 7896.59 | 0.071971 | 9039.61 | 0.078334 | 10131 | 0.088542 | 10259.5 | 0.10831 | 10479.3 | 0.15191 | 11257.1 | 0.19857
12468 | 0.034212 | 12732.6 | 0.034212 | 12938 | 0.03411 | 13398.9 | 0.033906 | 12860.6 | 0.034522 | 12196.7 | 0.035219 | 12912.2 | 0.035114 | 12886.4 | 0.036002 | 13107.3 | 0.036988 | 6043.14 | 0.061629 | 6254.45 | 0.071889 | 7465.51 | 0.066276 | 6615.59 | 0.087986 | 7869.49 | 0.09349 | 8704.24 | 0.10868 | 8967.41 | 0.13355 | 9233.25 | 0.1886 | 9969.88 | 0.24668
11036.1 | 0.035008 | 11304.1 | 0.034904 | 11509.5 | 0.034904 | 11967.2 | 0.034695 | 11440.6 | 0.035325 | 10763.6 | 0.036183 | 11486.5 | 0.036075 | 11452 | 0.03721 | 11671.7 | 0.038613 | 5071.52 | 0.072966 | 5364.36 | 0.085945 | 6487.99 | 0.077088 | 5752.65 | 0.10543 | 6878.36 | 0.11171 | 7551.53 | 0.13317 | 7923.77 | 0.16345 | 8210.24 | 0.23057 | 8916.19 | 0.30383
9603.93 | 0.036002 | 9876.64 | 0.035787 | 10076.1 | 0.035787 | 10539.9 | 0.035609 | 10005.8 | 0.036401 | 9329.42 | 0.037509 | 10056 | 0.037397 | 10025.9 | 0.038807 | 10248.9 | 0.040633 | 4489 | 0.083616 | 4672.65 | 0.10275 | 5551.93 | 0.093383 | 4908.6 | 0.13142 | 5967.46 | 0.13758 | 6726.41 | 0.15921 | 6878.36 | 0.208 | 7388.93 | 0.28075 | 8084.24 | 0.36826
8175.75 | 0.037099 | 8450.05 | 0.036877 | 8646.66 | 0.036803 | 9108.18 | 0.036693 | 8577.76 | 0.037697 | 7902.45 | 0.039197 | 8629.38 | 0.039118 | 8594.93 | 0.041001 | 8812.51 | 0.043406 | 3950.69 | 0.097927 | 4016.87 | 0.12677 | 4753.64 | 0.11449 | 4297.77 | 0.16067 | 5195.01 | 0.16994 | 5988.01 | 0.19231 | 6077.85 | 0.25913 | 6638.37 | 0.34342 | 7057.97 | 0.47974
6740.76 | 0.038497 | 7015.86 | 0.038305 | 7215.08 | 0.038191 | 7684.25 | 0.038 | 7143.29 | 0.039393 | 6469.98 | 0.041662 | 7200.66 | 0.041371 | 7164.75 | 0.044194 | 7382.95 | 0.047636 | 3484.91 | 0.11614 | 3523.05 | 0.15374 | 4035.32 | 0.14502 | 3694.59 | 0.20434 | 4611.49 | 0.20504 | 5327.61 | 0.23403 | 5339.83 | 0.32767 | 5916.41 | 0.42931 | 6344.66 | 0.5963
5313.09 | 0.04031 | 5585.49 | 0.040108 | 5784.45 | 0.040028 | 6253.7 | 0.039829 | 5715.45 | 0.041871 | 5043.87 | 0.045494 | 5767.12 | 0.044997 | 5732.62 | 0.049382 | 7265.76 | 0.048067 | 3097.02 | 0.13727 | 3049.49 | 0.19253 | 3488.91 | 0.18182 | 3208.99 | 0.25883 | 4039.94 | 0.25691 | 4737.33 | 0.28791 | 4710.28 | 0.41672 | 5245.85 | 0.54412 | 5609.47 | 0.7671
3885.19 | 0.042974 | 4154.42 | 0.042802 | 4354.34 | 0.042589 | 4821.92 | 0.042292 | 4285.22 | 0.045998 | 3611.68 | 0.05291 | 4336.96 | 0.0515 | 5524.39 | 0.05038 | 6980.86 | 0.049185 | 2747.58 | 0.1643 | 2581.28 | 0.25341 | 3004.41 | 0.23282 | 2779.24 | 0.33449 | 3602.64 | 0.31354 | 4283.02 | 0.34559 | 4183.6 | 0.52786 | 4696.8 | 0.68216 | 5068.61 | 0.95186
2452.66 | 0.047827 | 2726.92 | 0.047398 | 2924.64 | 0.047209 | 3391.16 | 0.046693 | 2855.29 | 0.054794 | 3533.09 | 0.053388 | 4263.85 | 0.052018 | 5286.59 | 0.05181 | 6640.4 | 0.050784 | 2445.96 | 0.19676 | 2208.86 | 0.33106 | 2660.85 | 0.28774 | 2440.37 | 0.42249 | 3181.54 | 0.39197 | 3852.36 | 0.41816 | 3773.73 | 0.64791 | 4178.81 | 0.86756 | 4530.33 | 1.2175
1023.44 | 0.064045 | 1295.86 | 0.061719 | 1495.07 | 0.060376 | 1960.45 | 0.057893 | 2779.23 | 0.055623 | 3421.82 | 0.054412 | 4113.08 | 0.053122 | 5038.83 | 0.053228 | 6335.53 | 0.052279 | 2177.45 | 0.23903 | 1931.77 | 0.42104 | 2387.82 | 0.34717 | 2158.83 | 0.53302 | 2846.92 | 0.48111 | 3461.04 | 0.51473 | 3321.2 | 0.84163 | 3677.7 | 1.1347 | 4124.12 | 1.5021
969.646 | 0.065601 | 1233.89 | 0.063218 | 1456.7 | 0.061227 | 1921.63 | 0.058474 | 2654.28 | 0.05686 | 3261.45 | 0.055901 | 3955.76 | 0.054304 | 4788.29 | 0.055014 | 5848.43 | 0.055345 | 2003.9 | 0.27549 | 1690.41 | 0.53823 | 2128.13 | 0.4276 | 1942.87 | 0.65499 | 2546.03 | 0.60042 | 3088.17 | 0.64569 | 2896.26 | 1.1282 | 3253.41 | 1.4597 | 3621.26 | 2.0368
886.19 | 0.068689 | 1144.73 | 0.065667 | 1374.61 | 0.063029 | 1844.43 | 0.059775 | 2514.75 | 0.058591 | 3074.59 | 0.057893 | 3740.33 | 0.056069 | 4500.43 | 0.057374 | 5496.84 | 0.057893 | 1810.69 | 0.3288 | 1474.97 | 0.69996 | 1894.51 | 0.53302 | 1750.52 | 0.80765 | 2300.55 | 0.73444 | 2816.1 | 0.7746 | 2563.59 | 1.4748 | 2941.41 | 1.8217 | 3260.87 | 2.6247
820.514 | 0.071707 | 1060.96 | 0.06862 | 1294.56 | 0.065078 | 1763.27 | 0.061288 | 2377.79 | 0.060618 | 2912.97 | 0.059895 | 3543.71 | 0.058008 | 4242.59 | 0.059895 | 5171.55 | 0.060618 | 1621.18 | 0.39876 | 1320.6 | 0.87154 | 1710.86 | 0.65014 | 1584.45 | 0.98737 | 2070.41 | 0.90873 | 2547.49 | 0.95022 | 2280.87 | 1.9005 | 2725.64 | 2.1605 | 2927.96 | 3.4428
765.808 | 0.074708 | 975.481 | 0.072211 | 1191.45 | 0.068278 | 1668.91 | 0.063345 | 2225.93 | 0.063218 | 2737.85 | 0.062401 | 3360.78 | 0.060075 | 3983.55 | 0.06284 | 4831.58 | 0.064238 | 1474.13 | 0.47618 | 1162.9 | 1.1237 | 1539.72 | 0.80258 | 1416.19 | 1.2514 | 1877.23 | 1.1084 | 2374.18 | 1.1021 | 2075.16 | 2.3854 | 2494.07 | 2.6458 | 2716.29 | 4.2234
701.297 | 0.07909 | 887.076 | 0.076753 | 1100.95 | 0.071779 | 1560.76 | 0.065798 | 2071.29 | 0.066393 | 2568.12 | 0.065274 | 3174.57 | 0.062589 | 3710.52 | 0.066592 | 4554.76 | 0.067464 | 1304.06 | 0.60145 | 1044.77 | 1.3984 | 1385.69 | 0.99247 | 1273.79 | 1.5564 | 1655.91 | 1.4456 | 2176.21 | 1.3251 | 1906.49 | 2.9431 | 2300.55 | 3.1959 | 2537.3 | 5.1485
634.559 | 0.084825 | 807.49 | 0.082236 | 974.506 | 0.078147 | 1453.79 | 0.068895 | 1944.83 | 0.069518 | 2404.09 | 0.068689 | 3010.7 | 0.065143 | 3470.06 | 0.070498 | 4150.27 | 0.073743 | 1161.57 | 0.75274 | 918.963 | 1.8374 | 1268.69 | 1.192 | 1168.24 | 1.866 | 1499.68 | 1.8082 | 1956.27 | 1.6833 | 1749.52 | 3.6813 | 2057.41 | 4.3386 | 2376.9 | 6.2977
573.026 | 0.09189 | 744.662 | 0.087496 | 854 | 0.086452 | 1350.09 | 0.072645 | 1815.16 | 0.073302 | 2241.56 | 0.072718 | 2807.16 | 0.068827 | 3235.47 | 0.075158 | 3831.18 | 0.079805 | 1025.21 | 0.97056 | 818.083 | 2.3786 | 1154.27 | 1.453 | 1051.98 | 2.3623 | 1332.75 | 2.3637 | 1755.54 | 2.1841 | 1618.39 | 4.5653 | 1910.86 | 5.3959 | 2235.59 | 7.7079
509.755 | 0.10125 | 686.037 | 0.093934 | 761.988 | 0.095736 | 1267.66 | 0.076065 | 1689.06 | 0.077679 | 2100.49 | 0.076753 | 2638.4 | 0.0725 | 2971.82 | 0.08158 | 3582.9 | 0.085763 | 888.425 | 1.3071 | 730.784 | 3.0916 | 1070.21 | 1.7076 | 934.357 | 3.1075 | 1189.17 | 3.0863 | 1598.13 | 2.7619 | 1503.12 | 5.7466 | 1765.62 | 7.0818 | 2120.83 | 9.2839
457.113 | 0.11235 | 637.74 | 0.10024 | 692.931 | 0.10465 | 1170.2 | 0.081092 | 1557.64 | 0.083395 | 1937.06 | 0.082813 | 2411.32 | 0.078617 | 2743.33 | 0.088907 | 3314.06 | 0.093559 | 812.479 | 1.586 | 658.434 | 4.0091 | 967.028 | 2.1507 | 855.464 | 3.8826 | 1092.51 | 3.8318 | 1454.83 | 3.553 | 1416.19 | 7.1021 | 1633.3 | 9.3908 | 2008.5 | 11.5002
412.374 | 0.12478 | 586.358 | 0.1087 | 625.112 | 0.11658 | 1085.64 | 0.086366 | 1433.58 | 0.08998 | 1786.35 | 0.089531 | 2219.26 | 0.08525 | 2547.65 | 0.096312 | 3099.29 | 0.10145 | 743.451 | 1.9468 | 591.212 | 5.4021 | 839.926 | 3.0112 | 785.929 | 4.9718 | 984.353 | 5.1279 | 1323.63 | 4.5863 | 1325.9 | 9.1154 | 1551.23 | 11.6593 | 1916.34 | 14.0834
362.104 | 0.14411 | 535.891 | 0.11941 | 561.118 | 0.13158 | 983.316 | 0.094499 | 1316.76 | 0.098159 | 1662.25 | 0.096698 | 2075.44 | 0.09134 | 2326.05 | 0.10719 | 2878.22 | 0.11112 | 679.898 | 2.3882 | 535.74 | 7.4094 | 762.427 | 3.8759 | 731.203 | 6.2439 | 903.824 | 6.734 | 1220.92 | 5.7334 | 1249.22 | 11.5927 | 1465.71 | 15.2062 | 1796.23 | 18.7932
330.277 | 0.16119 | 496.673 | 0.12988 | 507.721 | 0.1485 | 892.415 | 0.10423 | 1209.46 | 0.1074 | 1559.2 | 0.10371 | 1898.71 | 0.10054 | 2121.6 | 0.12001 | 2565.55 | 0.12923 | 614.695 | 3.0337 | 489.102 | 10.4817 | 683.804 | 5.2406 | 688.126 | 7.7655 | 836.086 | 8.9654 | 1133.96 | 7.1921 | 1187.13 | 14.5755 | 1404.87 | 19.0968 | 1728.6 | 23.3998
293.222 | 0.1884 | 456.656 | 0.14296 | 474.343 | 0.162 | 793.879 | 0.11799 | 1129.95 | 0.116 | 1456.7 | 0.11201 | 1735.29 | 0.11167 | 1942.88 | 0.13518 | 2363.57 | 0.14483 | 550.36 | 4.0436 | 452.186 | 14.7349 | 626.067 | 6.9057 | 639.477 | 10.4159 | 784.13 | 11.626 | 1064.71 | 8.9142 | 1127.48 | 19.6963 | 1348.11 | 25.6442 | 1674.03 | 29.3533
253.898 | 0.22989 | 416.935 | 0.16039 | 440.95 | 0.1785 | 731.378 | 0.13014 | 1038.91 | 0.12846 | 1359.57 | 0.12158 | 1598.67 | 0.12342 | 1773.89 | 0.15318 | 2162.3 | 0.16461 | 496.441 | 5.4083 | 429.465 | 19.2946 | 571.238 | 9.5535 | 606.997 | 13.1711 | 743.877 | 14.8195 | 993.416 | 11.5795 | 1085.03 | 26.6926 | 1311.55 | 34.4559 | 1631.43 | 37.2667
221.613 | 0.28219 | 379.909 | 0.18174 | 400.187 | 0.2041 | 673.798 | 0.14455 | 967.708 | 0.14041 | 1256.3 | 0.13397 | 1466.93 | 0.13791 | 1627.71 | 0.17253 | 1988.09 | 0.18672 | 456.088 | 7.0576 | 406.486 | 28.1843 | 533.596 | 12.596 | 578.151 | 16.8276 | 704.882 | 19.7754 | 944.581 | 14.3274 | 1054.39 | 34.1223 | 1280.37 | 44.2994 | 1589 | 49.8149
199.923 | 0.33083 | 345.133 | 0.20656 | 363.919 | 0.23406 | 615.805 | 0.162 | 901.384 | 0.1541 | 1162.03 | 0.1491 | 1384.27 | 0.14969 | 1504.07 | 0.19434 | 1826.08 | 0.21306 | 418.297 | 9.4935 | 391.854 | 39.8025 | 503.025 | 16.8855 | 554.156 | 22.3397 | 679.898 | 25.454 | 902.272 | 17.9212 | 1021.69 | 47.831 | 1254.24 | 59.8288 | 1558.35 | 65.6421
178.561 | 0.39885 | 316.06 | 0.235 | 334.264 | 0.26629 | 554.979 | 0.18672 | 838.765 | 0.16997 | 1080.23 | 0.16445 | 1297.15 | 0.16363 | 1391.21 | 0.21846 | 1716.3 | 0.23524 | 388.501 | 12.7264 | 382.101 | 53.5712 | 475.565 | 23.8324 | 536.354 | 29.6064 | 662.217 | 33.2355 | 866.809 | 23.0146 | 999.123 | 66.0567 | 1234.28 | 79.7453 | 1535.31 | 85.0739
163.029 | 0.46387 | 290.886 | 0.26576 | 305.494 | 0.30662 | 506.706 | 0.21306 | 772.731 | 0.19049 | 1008.2 | 0.18211 | 1219.17 | 0.17939 | 1279.12 | 0.25003 | 1568.58 | 0.27221 | 361.449 | 17.5959 | 370.675 | 85.0252 | 458.446 | 32.7071 | 524.505 | 37.395 | 650.561 | 41.9307 | 839.926 | 29.1524 | 987.177 | 88.5013 | 1221.62 | 104.422 | 1517.83 | 109.754
150.194 | 0.53464 | 266.382 | 0.3057 | 280.881 | 0.35234 | 450.308 | 0.25381 | 721.932 | 0.21137 | 926.979 | 0.20594 | 1144.73 | 0.19688 | 1179.6 | 0.28503 | 1478.71 | 0.30054 | 343.878 | 23.0542 | 366.033 | 124.127 | 443.719 | 46.8554 | 512.33 | 49.5022 | 640.21 | 51.526 | 817.615 | 37.2028 | 979.292 | 117.021 | 1215.34 | 128.759 | 1508.29 | 145.789
139.76 | 0.60825 | 247.381 | 0.34364 | 258.509 | 0.40326 | 406.235 | 0.29905 | 668.43 | 0.23808 | 817.238 | 0.24978 | 1068.41 | 0.21868 | 1094.36 | 0.32233 | 1402.38 | 0.33016 | 331.499 | 30.171 | 362.486 | 176 | 435.66 | 62.4532 | 503.89 | 64.3401 | 629.663 | 70.4304 | 801.845 | 46.3221 | 973.698 | 156.961 | 1210.48 | 165.165 | 1503.98 | 197.347
121.259 | 0.78493 | 226.996 | 0.39567 | 238.873 | 0.46155 | 379.529 | 0.33448 | 623.24 | 0.26523 | 735.044 | 0.29696 | 984.3 | 0.24904 | 1021.4 | 0.36234 | 1303.65 | 0.37525 | 322.509 | 39.8481 | 362.486 | 262.892 | 430.204 | 83.0055 | 497.01 | 80.941 | 621.422 | 100.263 | 788.183 | 57.9414 | 972.026 | 199.391 | 1205.63 | 218.265 | 1501.4 | 248.408
107.87 | 0.97613 | 207.666 | 0.45925 | 224.288 | 0.51625 | 340.335 | 0.40125 | 575.898 | 0.30054 | 668.43 | 0.34675 | 924.202 | 0.27605 | 952.348 | 0.40854 | 1217.95 | 0.42521 | 312.865 | 57.8751 | 362.694 | 383.356 | 426.768 | 111.783 | 492.193 | 103.588 | 616.458 | 137.599 | 774.754 | 73.8996 | 973.14 | 263.495 | 1200.81 | 289.594 | 1499.68 | 342.671
97.5079 | 1.1816 | 189.224 | 0.5384 | 210.594 | 0.57455 | 309.182 | 0.47418 | 541.277 | 0.33348 | 605.425 | 0.41018 | 860.859 | 0.31063 | 888.852 | 0.46109 | 1129.95 | 0.48911 | 307.534 | 80.7097 | 363.734 | 551.076 | 425.06 | 164.598 | 490.224 | 137.127 | 612.586 | 184.141 | 765.49 | 97.045 | 974.814 | 356.68 | 1203.56 | 391.338 | 1503.98 | 441.829
89.2939 | 1.4103 | 165.825 | 0.68855 | 196.946 | 0.64458 | 288.28 | 0.53625 | 502.669 | 0.37713 | 549.457 | 0.48765 | 803.463 | 0.34883 | 824.627 | 0.52458 | 1054.61 | 0.5559 | 304.205 | 121.04 | 363.317 | 600.484 | 425.06 | 225.504 | 489.382 | 186.688 | 609.785 | 262.892 | 760.247 | 128.171 | 977.05 | 449.224 | 1205.63 | 481.993 | 1500.54 | 521.312
81.3641 | 1.6953 | 148.403 | 0.841 | 178.919 | 0.76862 | 270.408 | 0.5992 | 465.881 | 0.42992 | 500.662 | 0.5757 | 749.893 | 0.3937 | 765.808 | 0.60281 | 969.646 | 0.65236 | 302.988 | 156.602 |  |  | 426.279 | 327.52 | 488.262 | 235.8 | 606.65 | 377.261 | 755.904 | 171.72 | 978.17 | 522.806 | 1205.63 | 518.04
75.1837 | 2.0014 | 134.684 | 1.0099 | 166.489 | 0.87883 | 254.915 | 0.66222 | 430.063 | 0.49502 | 460.324 | 0.6662 | 702.701 | 0.44124 | 723.377 | 0.6662 | 915.922 | 0.73333 | 301.603 | 225.891 |  |  | 427.257 | 437.049 | 488.262 | 303.859 | 605.955 | 481.166 | 752.879 | 233.65
70.2411 | 2.3206 | 122.233 | 1.2224 | 155.856 | 0.99984 | 236.496 | 0.75718 | 398.191 | 0.566 | 420.705 | 0.7818 | 640.296 | 0.52248 | 675.823 | 0.7534 | 854.854 | 0.84269 | 301.43 | 332.622 |  |  | 427.502 | 535.528 | 487.424 | 392.909 | 606.997 | 593.988 | 753.742 | 314.116
66.283 | 2.6587 | 110.822 | 1.4931 | 145.464 | 1.1466 | 222.278 | 0.85201 | 368.312 | 0.64846 | 387.583 | 0.91014 | 582.268 | 0.62428 | 622.617 | 0.88059 | 803.463 | 0.95872 | 301.948 | 498.549 |  |  | 428.728 | 593.988 | 487.424 | 504.289 |  |  | 753.311 | 405.475
62.423 | 3.0582 | 99.9763 | 1.8623 | 134.146 | 1.3537 | 206.217 | 0.98102 | 325.685 | 0.81533 | 362.104 | 1.0334 | 532.153 | 0.74218 | 583.434 | 0.99287 | 743.918 | 1.1296 | 302.294 | 597.74 |  |  |  |  | 487.983 | 590.936 |  |  | 755.039 | 526.711
59.1416 | 3.4933 | 93.4974 | 2.153 | 124.827 | 1.5712 | 194.402 | 1.1006 | 297.654 | 0.96256 | 337.961 | 1.1816 | 497.667 | 0.84691 | 551.108 | 1.1105 | 698.497 | 1.2851 | [10 empty] | 755.471 | 591.274
55.6974 | 4.0384 | 87.3509 | 2.5114 | 114.77 | 1.8905 | 183.081 | 1.2397 | 272.307 | 1.1455 | 314.483 | 1.3632 | 468.217 | 0.95584 | 516.426 | 1.2584 | 649.973 | 1.4916
52.1401 | 4.8251 | 82.1818 | 2.8946 | 108.519 | 2.1358 | 173.804 | 1.3797 | 252.379 | 1.3296 | 292.929 | 1.5775 | 437.874 | 1.1006 | 491.239 | 1.3907 | 610.288 | 1.7055
49.1528 | 5.7078 | 77.2413 | 3.3597 | 103.124 | 2.3746 | 164.175 | 1.5494 | 235.316 | 1.5339 | 276.146 | 1.784 | 414.856 | 1.2322 | 468.685 | 1.5324 | 577.629 | 1.921
46.383 | 6.6982 | 73.7687 | 3.7842 | 98.3895 | 2.6244 | 155.544 | 1.7364 | 222.723 | 1.7261 | 257.735 | 2.0685 | 395.018 | 1.3646 | 444.492 | 1.7209 | 551.66 | 2.1401
44.1651 | 7.7822 | 69.6814 | 4.4099 | 93.3106 | 2.9768 | 147.958 | 1.9345 | 209.334 | 1.9716 | 242.968 | 2.3699 | 372.759 | 1.5525 | 420.284 | 1.952 | 527.385 | 2.3604
42.2217 | 8.8982 | 66.0845 | 5.0929 | 89.2939 | 3.3329 | 139.76 | 2.1986 | 196.749 | 2.2475 | 229.736 | 2.6962 | 355.289 | 1.7278 | 399.387 | 2.2008 | 498.165 | 2.7043
40.6474 | 10.2353 | 62.548 | 5.9706 | 85.1091 | 3.7729 | 132.414 | 2.4964 | 183.081 | 2.6614 | 219.627 | 3.0157 | 335.268 | 1.9716 | 381.813 | 2.4543 | 471.034 | 3.0828
39.3279 | 11.8088 | 59.557 | 7.0065 | 81.8537 | 4.2032 | 126.714 | 2.7783 | 174.327 | 2.9798 | 207.666 | 3.4793 | 322.445 | 2.1551 | 362.829 | 2.7727 | 446.273 | 3.4933
37.8236 | 14.4088 | 56.9364 | 8.214 | 78.4086 | 4.7249 | 120.413 | 3.1514 | 164.339 | 3.4275 | 197.933 | 3.9308 | 310.111 | 2.3628 | 344.1 | 3.1831 | 425.784 | 3.9505
36.6691 | 17.6872 | 54.5945 | 9.6296 | 75.5605 | 5.3113 | 114.77 | 3.5674 | 155.078 | 3.9783 | 189.792 | 4.4231 | 300.345 | 2.5724 | 328.63 | 3.6069 | 409.088 | 4.3879
35.6566 | 21.8422 | 52.6115 | 11.2779 | 73.3274 | 5.923 | 110.049 | 3.9902 | 148.998 | 4.4497 | 183.265 | 4.9079 | 287.416 | 2.8515 | 313.228 | 4.12 | 393.441 | 4.9079
35.0205 | 26.0195 | 50.9036 | 13.341 | 70.5932 | 6.8815 | 105.207 | 4.5305 | 144.161 | 4.8736 | 178.204 | 5.3486 | 278.643 | 3.0983 | 299.146 | 4.7486 | 378.014 | 5.5005
34.3271 | 32.65 | 49.6468 | 15.5466 | 68.1652 | 7.9474 | 101.183 | 5.0827 | 138.647 | 5.4078 | 171.56 | 6.0005 | 268.253 | 3.4207 | 287.992 | 5.3113 | 363.919 | 6.1217
33.816 | 39.3638 | 48.3726 | 18.65 | 65.6892 | 9.345 | 97.4105 | 5.7021 | 133.477 | 5.9945 | 165.99 | 6.7049 | 258.251 | 3.7956 | 278.364 | 5.9586 | 351.754 | 6.7723
33.4461 | 48.4653 | 47.5572 | 21.6899 | 63.5568 | 10.9336 | 94.0601 | 6.4163 | 128.243 | 6.7995 | 161.73 | 7.4249 | 249.868 | 4.1697 | 267.717 | 6.7995 | 337.961 | 7.6511
33.2128 | 60.1504 | 46.99 | 25.3263 | 62.0496 | 12.4764 | 91.0068 | 7.1983 | 123.585 | 7.7512 | 156.95 | 8.3716 | 240.791 | 4.6685 | 259.545 | 7.7048 | 328.63 | 8.4981
33.0802 | 79.0317 | 46.3367 | 29.7208 | 60.5781 | 14.4811 | 88.3171 | 8.0917 | 119.813 | 8.7307 | 151.856 | 9.4768 | 233.208 | 5.1544 | 251.371 | 8.9428 | 319.875 | 9.4673
33.0141 | 108.294 | 45.8298 | 34.7384 | 59.438 | 16.8246 | 85.8785 | 9.1783 | 115.808 | 10.225 | 147.81 | 10.8465 | 226.316 | 5.6851 | 244.186 | 10.2046 | 313.541 | 10.3485
33.0141 | 153.216 | 45.3284 | 40.9293 | 58.5531 | 19.4111 | 83.9259 | 10.39 | 112.273 | 11.8679 | 143.873 | 12.4391 | 219.847 | 6.2516 | 239.351 | 11.4712 | 304.884 | 11.8206
33.0141 | 221.152 | 44.9223 | 48.5623 | 57.6814 | 23.2858 | 81.6085 | 12.0956 | 109.173 | 13.6924 | 140.602 | 14.237 | 212.285 | 7.1195 | 233.675 | 12.9597 | 298.847 | 13.1687
33.0141 | 317.619 | 44.5643 | 58.724 | 56.9364 | 27.6561 | 79.6732 | 14.025 | 106.477 | 16.0361 | 136.993 | 16.7407 | 204.779 | 8.1079 | 229.736 | 14.5101 | 292.052 | 14.7884
32.9811 | 467.712 | 44.3864 | 72.519 | 56.3135 | 33.4097 | 77.9396 | 16.0682 | 104.578 | 18.3356 | 134.012 | 19.4305 | 198.528 | 9.2336 | 225.638 | 16.2297 | 285.411 | 16.8752
32.9481 | 545.582 | 44.1651 | 91.6383 | 55.7532 | 40.1189 | 76.856 | 18.135 | 102.507 | 21.4311 | 130.312 | 23.5434 | 192.276 | 10.6317 | 221.834 | 18.1895 | 279.76 | 19.0648
32.9152 | 599.954 | 44.1651 | 121.613 | 55.3642 | 49.3949 | 75.4095 | 21.3456 | 100.477 | 25.1497 | 127.987 | 27.8782 | 187.154 | 12.1319 | 216.574 | 21.3669 | 273.399 | 22.0397
|  | 44.1651 | 157.095 | 55.1984 | 62.4801 | 74.1384 | 24.8497 | 98.5864 | 29.1906 | 125.578 | 33.0442 | 182.168 | 14.3657 | 213.136 | 24.8 | 266.648 | 26.0716
|  | 44.1651 | 198.314 | 55.1984 | 81.9287 | 73.1809 | 29.074 | 97.4105 | 33.6444 | 123.709 | 38.7778 | 178.383 | 16.6239 | 209.334 | 29.5134 | 262.154 | 29.7208
|  | 44.1651 | 274.198 | 55.1984 | 111.146 | 72.0913 | 34.3928 | 95.8643 | 39.9188 | 122.111 | 45.6885 | 174.501 | 19.295 | 204.984 | 36.1923 | 257.735 | 34.7384
|  | 44.1651 | 357.041 | 55.1984 | 144.005 | 71.1602 | 41.382 | 94.6261 | 46.7983 | 120.413 | 55.5258 | 170.193 | 23.2858 | 201.126 | 44.073 | 253.644 | 39.3245
|  | 44.0768 | 437.402 | 55.1984 | 187.889 | 70.3817 | 50.3424 | 93.404 | 56.0839 | 119.096 | 65.7493 | 167.491 | 27.7392 | 197.736 | 54.0467 | 249.868 | 45.4152
|  | 44.0328 | 541.776 | 55.1984 | 253.623 | 69.5422 | 61.3655 | 92.6597 | 65.9468 | 117.558 | 81.8468 | 164.668 | 33.2763 | 195.182 | 63.4878 | 246.148 | 54.4808
|  | 43.9888 | 599.954 | 55.1984 | 345.451 | 68.9881 | 73.9101 | 91.8295 | 77.312 | 116.155 | 103.218 | 162.379 | 39.9987 | 192.853 | 74.2805 | 242.968 | 63.6149
|  |  |  | 55.1984 | 466.777 | 68.3016 | 90.9081 | 91.0978 | 92.0056 | 115.115 | 126.83 | 160.442 | 47.08 | 190.744 | 87.169 | 239.59 | 76.3898
|  |  |  | 55.1984 | 566.713 | 67.8252 | 113.618 | 90.5529 | 108.728 | 113.514 | 168.149 | 158.528 | 56.365 | 188.28 | 102.601 | 236.26 | 91.6383
|  |  |  | 55.1432 | 599.954 | 67.4195 | 140.731 | 90.1012 | 131.611 | 112.723 | 205.172 | 156.48 | 67.7516 | 186.78 | 118.019 | 232.742 | 113.732
[6 empty] | 67.0162 | 180.161 | 89.7415 | 152.91 | 112.16 | 254.895 | 154.768 | 80.3867 | 185.106 | 136.982 | 229.736 | 135.89
[6 empty] | 66.7486 | 228.572 | 88.8486 | 188.077 | 111.601 | 314.458 | 152.312 | 103.012 | 183.631 | 161.233 | 227.223 | 161.717
[6 empty] | 66.4822 | 295.258 | 88.5824 | 239.332 | 111.155 | 384.849 | 150.345 | 130.692 | 181.804 | 191.684 | 224.512 | 196.733
[6 empty] | 66.283 | 365.714 | 88.1406 | 310.086 | 110.49 | 487.287 | 148.254 | 168.991 | 180.356 | 226.75 | 222.278 | 237.425
[6 empty] | 66.2168 | 452.077 | 88.0525 | 416.069 | 110.27 | 570.124 | 146.779 | 205.789 | 178.919 | 269.307 | 220.507 | 280.858
[6 empty] | 66.0845 | 540.153 | 88.0525 | 527.872 | 110.049 | 599.954 | 145.464 | 269.307 | 178.026 | 311.641 | 218.75 | 330.581
[6 empty] | 66.0845 | 599.954 | 88.0525 | 574.128 |  |  | 144.45 | 324.359 | 176.961 | 372.357 | 217.007 | 414.408
[8 empty] | 88.0525 | 599.954 |  |  | 143.585 | 405.797 | 175.903 | 451.625 | 215.925 | 497.131
[12 empty] | 143.012 | 502.127 | 175.2 | 532.111 | 215.709 | 566.713
[12 empty] | 142.584 | 572.409 | 174.501 | 574.128 | 215.278 | 599.954
[12 empty] | 142.584 | 599.954 | 173.978 | 599.954