## 119_44S4
S&C Power Fuses - Type SM-4 (15E thru 200E) and SM-5 (15E thru 300E) (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SM-4 (15E thru 200E) and SM-5 (15E thru 300E) (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SM-4 (15E thru 200E) and SM-5 (15E thru 300E) (34.5 and 46 kV)
Slow Speed (TCC 119-4-4) | [9 empty] | Slow Speed (TCC 119-4-4) | [9 empty] | Slow Speed (TCC 119-4-4)
Total Clearing Time-Current Characteristic Curves Dated March 18, 1985 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated March 18, 1985 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated March 18, 1985
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
25262.9 | 0.015531 | 25262.9 | 0.015776 | 25262.9 | 0.015629 | 25289.2 | 0.015711 | 25210.4 | 0.015892 | 25262.9 | 0.015875 | 25262.9 | 0.016008 | 25289.2 | 0.016008 | 25236.6 | 0.016363 | 25236.6 | 0.016673 | 25262.9 | 0.017132 | 25262.9 | 0.017493 | 25289.2 | 0.018372 | 25210.4 | 0.020563 | 25236.6 | 0.02333
20135 | 0.016517 | 14719.9 | 0.018106 | 19968.1 | 0.016569 | 18798.4 | 0.017025 | 19074.3 | 0.017007 | 18088.3 | 0.017329 | 20451.8 | 0.016813 | 20240 | 0.017025 | 20838.5 | 0.017293 | 21122.4 | 0.017974 | 21299 | 0.018858 | 21499.4 | 0.019396 | 20537.1 | 0.021041 | 20198 | 0.024503 | 19495.8 | 0.029906
13086.8 | 0.018545 | 8839.69 | 0.020521 | 13742.8 | 0.018277 | 12449.1 | 0.018936 | 15123.7 | 0.018087 | 13223.7 | 0.019095 | 14628.3 | 0.01843 | 15013.9 | 0.018936 | 16870 | 0.018877 | 15186.8 | 0.021085 | 16608.7 | 0.021937 | 17568.8 | 0.021983 | 14998.3 | 0.026859 | 15313.7 | 0.031475 | 15092.2 | 0.040388
9139.04 | 0.020265 | 4773.82 | 0.02435 | 9880.96 | 0.019971 | 8339.24 | 0.020779 | 11324.2 | 0.019682 | 8960.1 | 0.021869 | 11230.3 | 0.020329 | 10694.2 | 0.021801 | 13196.2 | 0.020975 | 10930.5 | 0.026058 | 12167.3 | 0.027226 | 13699.9 | 0.026359 | 11756.5 | 0.033543 | 11622.7 | 0.042506 | 11793.3 | 0.05675
7268.84 | 0.021552 | 3007.37 | 0.028121 | 7367.85 | 0.021373 | 5650.49 | 0.0236 | 8711.83 | 0.021262 | 6482.57 | 0.025046 | 8066.09 | 0.023501 | 7530.65 | 0.026359 | 10441.2 | 0.0236 | 7990.89 | 0.033508 | 9263.53 | 0.03425 | 10727.6 | 0.032748 | 9389.71 | 0.043177 | 9253.89 | 0.056928 | 9244.26 | 0.081506
5727.46 | 0.023016 | 2535.49 | 0.03 | 5448.37 | 0.023649 | 4083.84 | 0.026775 | 6751.1 | 0.02333 | 4914.97 | 0.028744 | 6448.93 | 0.026249 | 5505.37 | 0.033057 | 8295.96 | 0.027368 | 6442.22 | 0.041455 | 7178.63 | 0.045158 | 8748.17 | 0.040684 | 7421.72 | 0.05825 | 7649.13 | 0.076162 | 7360.19 | 0.11903
4143.78 | 0.025046 | 1950.58 | 0.033648 | 3792.96 | 0.026636 | 3070.62 | 0.030378 | 5459.73 | 0.02552 | 3954.19 | 0.033195 | 5118.56 | 0.030157 | 4333.43 | 0.040769 | 6660.38 | 0.032748 | 5302.93 | 0.05226 | 5697.73 | 0.060922 | 7291.57 | 0.050491 | 6008.32 | 0.07883 | 6141.08 | 0.10758 | 5817.57 | 0.1788
3238 | 0.026943 | 1440.91 | 0.039472 | 2997.99 | 0.029197 | 2386.97 | 0.035009 | 4270.75 | 0.028564 | 3131.94 | 0.039389 | 4191.49 | 0.034827 | 3526.47 | 0.050544 | 5522.59 | 0.038899 | 4275.19 | 0.069192 | 4564.89 | 0.08445 | 6160.28 | 0.062794 | 4956.06 | 0.1058 | 5107.92 | 0.14727 | 4749.04 | 0.26249
2648.78 | 0.028624 | 1115.45 | 0.045966 | 2340.24 | 0.032645 | 1888.65 | 0.04043 | 3530.14 | 0.032004 | 2424.53 | 0.050281 | 3400.32 | 0.041759 | 2831.21 | 0.066225 | 4617.45 | 0.046886 | 3574.5 | 0.090093 | 3710.96 | 0.1178 | 5134.57 | 0.081252 | 3995.56 | 0.15242 | 4113.7 | 0.21687 | 4003.88 | 0.36387
1958.71 | 0.032038 | 831.751 | 0.057765 | 1794.75 | 0.037309 | 1506.86 | 0.048176 | 2807.73 | 0.037193 | 1880.81 | 0.06706 | 2718.6 | 0.052369 | 2277.76 | 0.088417 | 3999.72 | 0.056337 | 2970.04 | 0.12028 | 3042 | 0.16483 | 4187.13 | 0.11204 | 3368.62 | 0.2052 | 3461.02 | 0.3 | 3368.62 | 0.51448
1525.79 | 0.035598 | 614.423 | 0.079823 | 1380.72 | 0.044226 | 1122.44 | 0.064453 | 2323.25 | 0.043177 | 1405.37 | 0.098447 | 2200.86 | 0.06699 | 1828.69 | 0.12192 | 3418.06 | 0.068976 | 2498.82 | 0.16059 | 2575.38 | 0.22284 | 3519.13 | 0.14943 | 2755.63 | 0.29627 | 2825.32 | 0.44596 | 2963.87 | 0.6685
1228.81 | 0.039307 | 492.774 | 0.10646 | 1082.29 | 0.054147 | 906.792 | 0.082275 | 1904.44 | 0.051988 | 1086.8 | 0.14377 | 1743.21 | 0.092377 | 1517.87 | 0.16295 | 2951.56 | 0.083835 | 2133.21 | 0.21261 | 2151.04 | 0.30921 | 3032.51 | 0.19376 | 2282.51 | 0.42374 | 2357.35 | 0.64051 | 2646.02 | 0.84449
953.241 | 0.045584 | 395.622 | 0.1468 | 896.47 | 0.064993 | 722.73 | 0.111 | 1570.91 | 0.063917 | 895.538 | 0.19805 | 1427.48 | 0.12488 | 1217.35 | 0.23624 | 2493.62 | 0.10769 | 1776.17 | 0.29657 | 1826.79 | 0.42418 | 2572.7 | 0.2647 | 1918.37 | 0.59664 | 1983.33 | 0.92281 | 2289.64 | 1.1537
762.127 | 0.053251 | 313.355 | 0.21217 | 722.73 | 0.082275 | 589.984 | 0.14959 | 1302.55 | 0.080241 | 728.015 | 0.28209 | 1160.45 | 0.1733 | 982.449 | 0.35302 | 2076.26 | 0.14362 | 1513.14 | 0.40769 | 1546.58 | 0.58738 | 2191.72 | 0.36009 | 1603.95 | 0.8614 | 1739.58 | 1.2333 | 1970.98 | 1.6244
627.346 | 0.062532 | 251.314 | 0.30761 | 586.312 | 0.10893 | 481.62 | 0.2035 | 1066.63 | 0.10569 | 598.643 | 0.40727 | 955.227 | 0.24198 | 816.315 | 0.50019 | 1754.13 | 0.19055 | 1257.27 | 0.58128 | 1189.8 | 0.99687 | 1779.87 | 0.54373 | 1323.04 | 1.2913 | 1483.52 | 1.7329 | 1732.36 | 2.1846
494.83 | 0.079242 | 193.137 | 0.48935 | 463.909 | 0.15195 | 395.622 | 0.28594 | 874.356 | 0.14066 | 496.894 | 0.5886 | 788.756 | 0.34072 | 662.232 | 0.77364 | 1439.41 | 0.27056 | 1083.41 | 0.78502 | 976.334 | 1.5402 | 1546.58 | 0.72442 | 1111.97 | 1.9275 | 1287.72 | 2.4173 | 1522.62 | 2.9688
395.21 | 0.10459 | 152.817 | 0.77768 | 382.663 | 0.20671 | 321.95 | 0.41499 | 718.231 | 0.19095 | 398.1 | 0.92281 | 654.013 | 0.48327 | 538.352 | 1.1866 | 1176.25 | 0.39266 | 907.736 | 1.1228 | 822.284 | 2.2706 | 1329.95 | 0.99896 | 956.222 | 2.8091 | 1100.46 | 3.5487 | 1334.11 | 4.1542
322.621 | 0.13689 | 123.328 | 1.2295 | 311.405 | 0.28924 | 269.183 | 0.57946 | 607.429 | 0.25255 | 321.281 | 1.4392 | 535.558 | 0.7102 | 438.101 | 1.8662 | 974.303 | 0.56632 | 767.699 | 1.6227 | 681.813 | 3.6122 | 1076.67 | 1.5645 | 805.345 | 4.3904 | 955.227 | 5.2974 | 1198.5 | 5.581
267.508 | 0.18125 | 104.085 | 1.7732 | 250.792 | 0.42729 | 221.348 | 0.85513 | 503.662 | 0.35635 | 265.29 | 2.233 | 453.881 | 1.0021 | 360.624 | 2.9657 | 819.72 | 0.79574 | 670.554 | 2.2214 | 587.533 | 5.3865 | 927.793 | 2.2075 | 698.33 | 6.7481 | 864.404 | 7.2065 | 1094.75 | 7.4512
218.146 | 0.2515 | 91.3891 | 2.4274 | 195.361 | 0.6999 | 188.962 | 1.1817 | 418.928 | 0.50281 | 218.146 | 3.5598 | 390.712 | 1.3732 | 296.539 | 4.9604 | 678.275 | 1.1903 | 583.876 | 3.1738 | 502.615 | 8.759 | 761.334 | 3.5784 | 625.39 | 9.9376 | 783.03 | 10.4588 | 1007.29 | 10.0208
183.154 | 0.34001 | 79.6587 | 3.3683 | 158.156 | 1.0904 | 157.992 | 1.7239 | 345.2 | 0.75687 | 175.503 | 6.3122 | 330.436 | 1.9992 | 257.135 | 7.6881 | 568.881 | 1.7438 | 518.016 | 4.3904 | 449.649 | 14.0218 | 629.308 | 6.2991 | 563.577 | 15.7928 | 730.291 | 13.978 | 937.499 | 13.4768
151.865 | 0.47527 | 67.7917 | 5.2097 | 135.157 | 1.537 | 134.595 | 2.4889 | 280.918 | 1.1645 | 150.45 | 10.3935 | 287.125 | 2.7916 | 239.317 | 9.7935 | 482.623 | 2.5203 | 462.945 | 6.1433 | 403.523 | 24.9933 | 544.55 | 10.3719 | 530.013 | 23.6242 | 681.104 | 19.826 | 883.503 | 17.8431
129.511 | 0.64252 | 58.906 | 8.2275 | 114.187 | 2.247 | 115.622 | 3.5784 | 232.444 | 1.7493 | 133.063 | 17.0426 | 249.75 | 3.9554 | 212.544 | 15.5638 | 422.87 | 3.425 | 419.801 | 8.5335 | 384.66 | 37.9373 | 472.682 | 19.9713 | 507.873 | 34.1431 | 647.242 | 27.7708 | 836.961 | 23.6735
111.023 | 0.87316 | 51.9902 | 13.5049 | 97.6835 | 3.2782 | 96.6721 | 6.0039 | 191.935 | 2.6999 | 125.399 | 22.7059 | 218.374 | 5.8189 | 194.145 | 23.9468 | 372.06 | 4.7576 | 382.265 | 11.9157 | 369.36 | 58.799 | 444.531 | 33.2988 | 493.801 | 52.5333 | 626.693 | 39.4304 | 795.35 | 32.0044
91.1042 | 1.3198 | 47.5887 | 21.5968 | 84.7914 | 4.8226 | 85.2338 | 9.4522 | 160.645 | 4.1759 | 117.563 | 33.5079 | 196.585 | 8.2619 | 182.583 | 37.8977 | 330.78 | 6.6225 | 348.811 | 18.3913 | 362.505 | 86.6811 | 430.866 | 54.0906 | 482.623 | 81.1669 | 608.062 | 61.6897 | 761.334 | 48.4781
77.7746 | 1.876 | 44.8011 | 36.6916 | 73.1427 | 7.545 | 75.5409 | 16.9716 | 137.569 | 6.4386 | 113.122 | 48.4781 | 178.264 | 12.0784 | 176.418 | 60.1642 | 291.036 | 9.7222 | 327.697 | 27.916 | 359.874 | 122.178 | 423.751 | 81.1669 | 478.124 | 127.119 | 599.891 | 87.7732 | 738.7 | 69.6262
66.8111 | 2.7511 | 43.8326 | 60.542 | 64.0203 | 12.2306 | 70.5998 | 28.4452 | 122.051 | 9.4917 | 109.988 | 74.434 | 161.988 | 19.7023 | 174.229 | 94.03 | 265.014 | 13.7036 | 313.681 | 42.6397 | 358.752 | 170.248 | 420.675 | 126.458 | 477.13 | 195.181 | 595.536 | 135.19 | 729.532 | 97.1209
56.2109 | 4.3812 | 43.424 | 107.801 | 59.0902 | 19.3559 | 67.8623 | 43.7665 | 110.447 | 13.9634 | 108.623 | 121.036 | 152.182 | 30.8247 | 173.867 | 138.908 | 245.115 | 19.0952 | 303.407 | 67.2698 | 359.874 | 255.736 | 418.492 | 187.986 | 477.627 | 305.047 | 596.156 | 194.571 | 718.231 | 128.319
50.655 | 5.9354 | 43.3788 | 173.294 | 56.7398 | 29.1665 | 65.7763 | 78.8301 | 101.518 | 20.3924 | 108.623 | 193.761 | 146.129 | 49.5003 | 173.686 | 217.778 | 230.517 | 27.6551 | 299.33 | 94.1282 | 359.125 | 360.466 | 419.364 | 275.112 | 477.13 | 422.412 | 595.536 | 277.418 | 714.504 | 175.295
45.791 | 8.1591 | 43.4692 | 301.566 | 55.4555 | 43.7208 | 65.0953 | 125.538 | 94.1894 | 31.8711 | 108.623 | 311.479 | 143.417 | 72.0651 | 172.605 | 321.383 | 224.597 | 36.1219 | 297.157 | 134.487 | 356.89 | 523.145 | 417.187 | 409.822 | 480.119 | 587.377 | 598.643 | 401.36 | 713.76 | 246.309
42.2647 | 10.8364 | 43.4692 | 467.886 | 54.6534 | 66.5022 | 65.2309 | 188.97 | 89.9735 | 53.4176 | 108.963 | 466.424 | 141.637 | 116.453 | 172.246 | 479.249 | 220.429 | 47.5266 | 296.231 | 187.204 | 358.752 | 603.528 | 419.364 | 588.604 |  |  | 596.777 | 533.619 | 711.535 | 328.502
39.5002 | 14.7112 | 43.3788 | 596.019 | 54.3697 | 94.6205 | 65.2988 | 292.884 | 88.1202 | 82.4471 | 108.963 | 600.388 | 141.195 | 176.948 | 172.605 | 593.537 | 218.146 | 65.8807 | 296.539 | 268.589 | [6 empty] | 597.398 | 594.777 | 710.056 | 428.18
37.2639 | 20.4137 |  |  | 54.3697 | 139.053 | 65.163 | 423.736 | 86.8455 | 128.319 |  |  | 141.048 | 256.806 |  |  | 217.693 | 90.0927 | 297.157 | 357.097 | [8 empty] | 714.504 | 544.302
35.6702 | 29.2884 |  |  | 54.4263 | 208.659 | 65.0275 | 565.135 | 86.7552 | 201.808 |  |  | 141.048 | 359.339 |  |  | 218.146 | 124.235 | 296.231 | 463.997 | [8 empty] | 713.76 | 601.015
34.4301 | 41.025 |  |  | 54.5397 | 307.604 | 65.0953 | 592.3 | 86.8455 | 334.031 |  |  | 141.342 | 491.401 |  |  | 217.693 | 175.478 | 296.539 | 598.512
33.7208 | 58.1887 |  |  | 54.483 | 437.665 |  |  | 86.665 | 481.756 |  |  | 141.048 | 601.642 |  |  | 218.374 | 242.738
33.1985 | 90.9426 |  |  | 54.3131 | 600.388 |  |  | 86.936 | 602.899 | [6 empty] | 216.788 | 318.047
32.7183 | 136.181 | [14 empty] | 216.338 | 427.287
32.7183 | 208.659 | [14 empty] | 217.24 | 550.011
32.7524 | 280.913 | [14 empty] | 216.788 | 601.642
32.8206 | 376.219
32.7183 | 512.342
32.6503 | 597.264