## Total Clearing Data
S&C Fault Tamer Fuse Limiter | [9 empty] | S&C Fault Tamer Fuse Limiter
S&C Standard Speed (TCC 123-8-3) | [9 empty] | S&C Standard Speed (TCC 123-8-3)
Total Clearing Time-Current Characteristic Curves Dated September 29, 2003 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated September 29, 2003
Tolerance in Terms of Current: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance in Terms of Current: Curves are plotted to maximum test points. All variations are minus.
1A |  | 2A |  | 3A |  | 5A |  | 7A |  | 10A |  | 15A |  | 20A
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
750 | 0.01 | 750 | 0.01 | 750 | 0.01 | 750 | 0.01 | 750 | 0.01 | 750 | 0.01 | 750 | 0.01 | 750 | 0.01
729.4575 | 0.013932 | 729.4575 | 0.014205 | 725 | 0.015 | 725 | 0.015 | 725 | 0.015 | 720 | 0.0165 | 712.853 | 0.018644 | 710 | 0.0195
639.28 | 0.013979 | 612.374 | 0.014454 | 660.068 | 0.015171 | 691.14 | 0.01556 | 712.853 | 0.01682 | 702.288 | 0.020277 | 699.842 | 0.0244 | 700 | 0.023823
585.428 | 0.014134 | 554.099 | 0.01455 | 605.069 | 0.015311 | 624.12 | 0.016069 | 646.998 | 0.01735 | 662.051 | 0.021404 | 675 | 0.025 | 675 | 0.025
537.185 | 0.014319 | 496.381 | 0.014844 | 539.878 | 0.01556 | 562.473 | 0.016596 | 596.061 | 0.017986 | 614.214 | 0.022796 | 560 | 0.03 | 560 | 0.03
488.502 | 0.014535 | 450.493 | 0.015129 | 483.641 | 0.016069 | 506.408 | 0.017437 | 543.127 | 0.018965 | 554.099 | 0.024993 | 489 | 0.035 | 489 | 0.035
436.306 | 0.014829 | 407.216 | 0.015512 | 440.25 | 0.016444 | 458.217 | 0.018276 | 502.373 | 0.019877 | 513.035 | 0.026886 | 440 | 0.04 | 440 | 0.04
394.786 | 0.015144 | 368.096 | 0.016016 | 408.031 | 0.016854 | 405.59 | 0.01968 | 461.898 | 0.021064 | 467.941 | 0.029506 | 373 | 0.05 | 373 | 0.05
349.444 | 0.015574 | 331.406 | 0.016653 | 371.052 | 0.017647 | 361.891 | 0.021191 | 426.385 | 0.022614 | 422.565 | 0.032871 | 328 | 0.06 | 328 | 0.06
315.558 | 0.016 | 300.168 | 0.017385 | 335.742 | 0.018664 | 332.401 | 0.022728 | 392.817 | 0.024376 | 388.131 | 0.036255 | 296 | 0.07 | 296 | 0.07
286.96 | 0.016553 | 272.692 | 0.018276 | 307.152 | 0.01968 | 303.488 | 0.024596 | 365.528 | 0.026143 | 354.725 | 0.040512 | 273 | 0.08 | 273 | 0.08
261.476 | 0.017194 | 237.779 | 0.019818 | 278.758 | 0.020834 | 272.692 | 0.027129 | 338.777 | 0.028179 | 327.78 | 0.044997 | 255 | 0.09 | 255 | 0.09
234.708 | 0.018058 | 211.102 | 0.021469 | 245.021 | 0.022773 | 247.979 | 0.029832 | 311.171 | 0.030895 | 307.152 | 0.049136 | 240 | 0.1 | 240 | 0.1
210.681 | 0.019155 | 186.67 | 0.023467 | 220.819 | 0.024547 | 226.862 | 0.032772 | 286.387 | 0.034008 | 288.687 | 0.054033 | 192 | 0.15 | 192 | 0.15
187.981 | 0.020401 | 165.231 | 0.025961 | 197.027 | 0.026886 | 208.584 | 0.036111 | 266.758 | 0.037025 | 260.172 | 0.063345 | 164 | 0.2 | 164 | 0.2
168.737 | 0.021815 | 146.693 | 0.028806 | 179.171 | 0.029212 | 187.981 | 0.041165 | 246.989 | 0.04096 | 231.909 | 0.075761 | 148 | 0.25 | 148 | 0.25
152.832 | 0.023233 | 128.168 | 0.032707 | 164.736 | 0.031614 | 173.529 | 0.045722 | 232.141 | 0.044504 | 206.509 | 0.091431 | 134 | 0.3 | 134 | 0.3
136.776 | 0.025118 | 111.647 | 0.037697 | 152.527 | 0.034247 | 157.33 | 0.052593 | 217.531 | 0.048744 | 184.998 | 0.1109 | 125 | 0.35 | 125 | 0.35
117.842 | 0.028095 | 99.8177 | 0.042589 | 137.599 | 0.038305 | 139.121 | 0.062903 | 197.225 | 0.05652 | 166.391 | 0.13356 | 117 | 0.4 | 117 | 0.4
102.14 | 0.031582 | 89.0632 | 0.048598 | 127.02 | 0.041955 | 121.067 | 0.078382 | 175.273 | 0.067599 | 149.507 | 0.1633 | 104 | 0.5 | 104 | 0.5
90.6808 | 0.035114 | 88.7076 | 0.048842 | 119.145 | 0.045585 | 107.484 | 0.094405 | 156.701 | 0.081011 | 135.686 | 0.19629 | 95.8 | 0.6 | 95.8 | 0.6
80.5071 | 0.039275 | 78.3625 | 0.056803 | 113.108 | 0.048598 | 95.7122 | 0.11439 | 140.378 | 0.096988 | 122.896 | 0.23951 | 89.9 | 0.7 | 89.9 | 0.7
71.1895 | 0.044371 | 69.0856 | 0.066194 | 110.095 | 0.05043 | 85.9139 | 0.1364 | 126.386 | 0.11635 | 111.535 | 0.29137 | 84 | 0.8 | 84 | 0.8
65.5194 | 0.048259 | 62.0752 | 0.076676 | 98.0371 | 0.059596 | 77.0416 | 0.16593 | 115.047 | 0.13777 | 101.427 | 0.35128 | 80 | 0.9 | 80 | 0.9
58.1105 | 0.055069 | 54.2361 | 0.091158 | 88.0008 | 0.069449 | 68.6037 | 0.20328 | 105.145 | 0.16249 | 91.0443 | 0.43685 | 76 | 1 | 77 | 1
50.5188 | 0.064431 | 47.5768 | 0.10946 | 79.2293 | 0.08158 | 60.2406 | 0.25713 | 97.0616 | 0.18992 | 81.479 | 0.54708 | 64 | 1.5 | 68.3 | 1.5
44.1391 | 0.075308 | 42.2391 | 0.1291 | 72.6277 | 0.09384 | 54.5079 | 0.30723 | 87.9128 | 0.22874 | 74.169 | 0.66354 | 56.6 | 2 | 63.2 | 2
39.0306 | 0.086972 | 37.8014 | 0.1515 | 64.6731 | 0.11359 | 48.6838 | 0.37675 | 80.1858 | 0.2744 | 67.178 | 0.8186 | 52.3 | 2.5 | 60.7845 | 2.5
34.5479 | 0.10064 | 33.8299 | 0.17832 | 57.4748 | 0.13819 | 43.3951 | 0.46619 | 72.121 | 0.33683 | 60.7244 | 1.0139 | 49.5 | 3 | 59.3735 | 2.851
30.9492 | 0.11554 | 30.58 | 0.2076 | 50.9246 | 0.16777 | 42.17 | 0.49949 | 65.3231 | 0.40977 | 56.4495 | 1.1982 | 47.5 | 3.5 | 57.49 | 3.5
27.6699 | 0.1333 | 27.6423 | 0.24362 | 44.5827 | 0.2078 | 39.3192 | 0.58265 | 59.1659 | 0.497 | 52.3183 | 1.4245 | 45.919 | 4 | 56.4667 | 4
24.7381 | 0.15441 | 24.7877 | 0.29108 | 39.5018 | 0.2533 | 36.6609 | 0.67695 | 54.4534 | 0.5891 | 48.7325 | 1.6801 | 43.822 | 5 | 54.9658 | 5
22.2278 | 0.17832 | 22.3616 | 0.34467 | 35.07 | 0.30815 | 34.3881 | 0.78024 | 50.1664 | 0.70036 | 45.3925 | 1.9834 | 42.4319 | 6 | 53.9874 | 6
19.8926 | 0.2076 | 20.1327 | 0.41141 | 31.5744 | 0.36782 | 32.2563 | 0.90108 | 46.1707 | 0.83264 | 42.3237 | 2.3487 | 41.1522 | 7 | 53.112 | 7
17.2075 | 0.25457 | 17.9636 | 0.4965 | 27.5319 | 0.46666 | 30.2868 | 1.0375 | 42.2391 | 1.0038 | 39.8191 | 2.7424 | 40.271 | 8 | 52.4557 | 8
14.8106 | 0.31438 | 16.0121 | 0.60704 | 24.3786 | 0.58792 | 28.7521 | 1.1675 | 39.0306 | 1.1934 | 37.09 | 3.2964 | 39.5542 | 9 | 51.8911 | 9
12.684 | 0.39488 | 14.3012 | 0.74441 | 22.236 | 0.7074 | 27.0777 | 1.3349 | 36.0298 | 1.426 | 34.5479 | 4.0303 | 38.9935 | 10 | 51.3325 | 10
11.016 | 0.48619 | 13.0703 | 0.87883 | 20.5264 | 0.82848 | 25.757 | 1.5051 | 33.0938 | 1.7209 | 32.2767 | 4.8981 | 37.2814 | 15.3109 | 49.7042 | 15 | y= -0.0003*b4 + 0.2325
9.9976 | 0.5643 | 11.7558 | 1.082 | 19.177 | 0.95489 | 24.4031 | 1.7174 | 30.58 | 2.0665 | 30.9587 | 5.5781 | 36.4832 | 20.6063 | 48.8194 | 20
8.9026 | 0.67695 | 10.7372 | 1.2928 | 17.8447 | 1.105 | 23.2827 | 1.9384 | 28.4272 | 2.4543 | 29.9239 | 6.2956 | 36.0241 | 25.527 | 48.1164 | 25
7.8566 | 0.83014 | 10.1524 | 1.4591 | 16.7887 | 1.2609 | 22.1251 | 2.2008 | 26.2679 | 2.9768 | 28.8369 | 7.1911 | 35.5789 | 30.4089 | 47.5108 | 30
7.0805 | 0.9889 | 9.7154 | 1.611 | 15.7322 | 1.4577 | 21.1938 | 2.4617 | 24.5901 | 3.539 | 27.9008 | 8.0917 | 35.0665 | 40.3645 | 46.59 | 41.6869
6.4646 | 1.1605 | 9.3345 | 1.7697 | 14.8457 | 1.6331 | 20.3424 | 2.726 | 22.9506 | 4.2795 | 27.1576 | 8.9696 | 34.8171 | 49.6592 | 46.248 | 50
5.8495 | 1.3921 | 8.9327 | 1.9696 | 14.0934 | 1.8578 | 19.7215 | 2.959 | 21.6574 | 5.0776 | 26.6375 | 9.9428 | 34.5058 | 60.3949 | 45.8345 | 60
5.2036 | 1.7469 | 8.5311 | 2.2386 | 13.4598 | 2.0512 | 19.2345 | 3.1514 | 20.3961 | 6.0973 | 26.0191 | 11.1322 | 34.379 | 69.024 | 45.5924 | 70
4.8893 | 1.9676 | 8.3396 | 2.3988 | 12.958 | 2.2856 | 18.6475 | 3.4551 | 19.9526 | 6.8131 | 25.421 | 12.5892 | 34.2604 | 80 | 45.4248 | 80
4.6243 | 2.2724 | 7.9623 | 2.8184 | 12.6312 | 2.4099 | 18.0782 | 3.8223 | 19.5434 | 7.5977 | 24.8767 | 14.6266 | 34.1344 | 90 | 45.2681 | 90
4.4131 | 2.6218 | 7.6779 | 3.2997 | 12.179 | 2.6669 | 17.6142 | 4.1864 | 19.1426 | 8.356 | 24.4339 | 16.6406 | 34.0716 | 100 | 45.0187 | 100
4.2193 | 3.0067 | 7.4738 | 3.7428 | 11.8191 | 2.9309 | 17.1965 | 4.6036 | 18.9671 | 9.0573 | 23.9548 | 19.6847 | 33 | 300 | 44 | 300
4.1299 | 3.2885 | 7.2618 | 4.3312 | 11.5272 | 3.155 | 16.705 | 5.201 | 18.578 | 9.9826 | 23.6153 | 23.0541
3.998 | 3.7056 | 7.0802 | 4.9523 | 11.2187 | 3.4914 | 16.2763 | 5.8524 | 18.2855 | 10.9665 | 23.3181 | 27.4632
3.9061 | 4.1365 | 6.892 | 5.7825 | 10.8777 | 3.9174 | 15.8903 | 6.6648 | 17.9055 | 12.5264 | 23.0246 | 32.7481
3.8225 | 4.6452 | 6.7088 | 6.7385 | 10.5522 | 4.5394 | 15.5757 | 7.3879 | 17.6213 | 14.166 | 22.8188 | 39.0502
3.7337 | 5.2585 | 6.6015 | 7.7357 | 10.1075 | 5.668 | 15.2368 | 8.3884 | 17.3589 | 16.0682 | 22.6148 | 47.696
3.6605 | 5.821 | 6.4602 | 8.9966 | 9.8388 | 6.6449 | 14.9351 | 9.6296 | 17.0834 | 18.4829 | 22.3971 | 59.9103
3.5444 | 6.8391 | 6.3569 | 10.3588 | 9.6127 | 7.79 | 14.6393 | 11.0435 | 16.8291 | 21.0278 | 22.2793 | 72.0852
3.4621 | 7.8605 | 6.2437 | 12.0353 | 9.3895 | 9.0961 | 14.3637 | 12.7667 | 16.6283 | 24.5778 | 22.257 | 90.0036
3.3888 | 8.9966 | 6.1326 | 14.337 | 9.2394 | 10.2329 | 14.1216 | 14.7294 | 16.4464 | 28.5268 | 22.1903 | 111.146
3.3461 | 9.8401 | 6.0234 | 16.9428 | 9.0249 | 12.3595 | 13.9253 | 17.0789 | 16.2991 | 33.6444 | 22.146 | 139.889
3.2805 | 11.5634 | 5.9271 | 20.7562 | 8.848 | 15.0314 | 13.7957 | 19.6062 | 16.1853 | 39.0892 | 22.0796 | 172.751
3.211 | 13.6105 | 5.831 | 25.527 | 8.6128 | 19.2752 | 13.6724 | 22.6202 | 16.1046 | 46.5184 | 22.0135 | 215.2782
3.1648 | 15.6715 | 5.759 | 30.0796 | 8.4595 | 23.2274 | 13.5252 | 26.0716 | 16.0403 | 55.9159 | 22.0543 | 243.922
3.1084 | 18.3654 | 5.697 | 35.1578 | 8.3089 | 28.987 | 13.4507 | 30.1097 | 15.9922 | 67.2118 | 22.0137 | 275.572
3.0693 | 21.3029 | 5.646 | 40.9703 | 8.2346 | 33.0442 | 13.3796 | 34.8428 | 15.9763 | 80.0658 | 22.0137 | 301.524
3.0314 | 24.4553 | 5.5956 | 48.6109 | 8.1638 | 38.1241 | 13.3304 | 40.1992 | 15.9922 | 95.7604
2.9933 | 29.1322 | 5.5455 | 59.2549 | 8.0826 | 43.7218 | 13.3059 | 46.5649 | 15.9763 | 120.644
2.9508 | 34.2555 | 5.496 | 70.6578 | 8.0262 | 49.9413 | 13.26 | 54.2633 | 15.9763 | 148.242
2.9244 | 39.7594 | 5.4468 | 84.7622 | 7.9863 | 57.8497 | 13.2112 | 64.3829 | 15.9763 | 190.157
2.893 | 46.1318 | 5.3981 | 99.3116 | 7.9587 | 67.2118 | 13.1869 | 77.933 | 15.9922 | 226.977
2.8618 | 53.1888 | 5.3499 | 126.4736 | 7.9149 | 78.8738 | 13.1657 | 92.8374 | 15.9763 | 259.784
2.8362 | 61.3655 | 5.3106 | 147.65 | 7.8876 | 93.2095 | 13.1415 | 111.146 | 15.9763 | 300.321
2.8006 | 75.4031 | 5.2825 | 172.405 | 7.8731 | 112.488 | 13.0931 | 139.33
2.7806 | 88.1332 | 5.2546 | 205.172 | 7.8731 | 131.874 | 13.069 | 172.233
2.7558 | 102.498 | 5.2353 | 249.348 | 7.8586 | 157.409 | 13.048 | 211.844
2.7261 | 122.223 | 5.2077 | 298.226 | 7.8315 | 194.776 | 13.024 | 249.598
2.7067 | 142.715 |  |  | 7.8315 | 238.376 | 13 | 299.721
2.6825 | 168.991 |  |  | 7.8171 | 268.232
2.6585 | 195.8845 |  |  | 7.8027 | 297.928
2.6396 | 226.524
2.6203 | 259.524
2.6016 | 301.223