## Sheet1
S&C Power Fuses - Type SMU-20 (25 and 34.5 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (25 and 34.5 kV)
"DR" Speed (TCC 175-2-4) | [9 empty] | "DR" Speed (TCC 175-2-4)
Total Clearing Time-Current Characteristic Curves Dated August 29, 2005 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 2005
Tolerance: | Curves are plotted to maximum test points. All variations are minus. | [8 empty] | Tolerance: | Curves are plotted to maximum test points. All variations are minus.
3DR |  | 4DR |  | 5DR |  | 7DR |  | 10DR |  | 15DR |  | 20DR
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
15770.9 | 0.01 | 15770.9 | 0.01 | 15770.9 | 0.01 | 15770.9 | 0.01 | 15770.9 | 0.01 | 15770.9 | 0.01 | 15770.9 | 0.01
15770.9 | 0.016161 | 15770.9 | 0.016161 | 15770.9 | 0.016161 | 15770.9 | 0.016161 | 15770.9 | 0.016161 | 15770.9 | 0.016161 | 15770.9 | 0.016161
15770.9 | 0.016161 | 15770.9 | 0.016161 | 15770.9 | 0.016161 | 15770.9 | 0.016161 | 15770.9 | 0.016161 | 15770.9 | 0.016161 | 15770.9 | 0.016161
5669.91 | 0.019997 | 5669.91 | 0.019997 | 5669.91 | 0.019997 | 5669.91 | 0.019997 | 5669.91 | 0.019997 | 5669.91 | 0.019997 | 5669.91 | 0.019997
4702.87 | 0.020938 | 4702.87 | 0.020938 | 4702.87 | 0.020938 | 4702.87 | 0.020938 | 4702.87 | 0.020938 | 4702.87 | 0.020938 | 4702.87 | 0.020938
4047.8 | 0.021858 | 4047.8 | 0.021858 | 4047.8 | 0.021858 | 4047.8 | 0.021858 | 4047.8 | 0.021858 | 4047.8 | 0.021858 | 4047.8 | 0.021858
3579.32 | 0.022796 | 3579.32 | 0.022796 | 3579.32 | 0.022796 | 3579.32 | 0.022796 | 3579.32 | 0.022796 | 3579.32 | 0.022796 | 3579.32 | 0.022796
3193.68 | 0.023679 | 3193.68 | 0.023679 | 3193.68 | 0.023679 | 3193.68 | 0.023679 | 3193.68 | 0.023679 | 3193.68 | 0.023679 | 3193.68 | 0.023679
2702.49 | 0.025118 | 2702.49 | 0.025118 | 2702.49 | 0.025118 | 2702.49 | 0.025118 | 2702.49 | 0.025118 | 2702.49 | 0.025118 | 2702.49 | 0.025118
2316.77 | 0.026459 | 2316.77 | 0.026459 | 2316.77 | 0.026459 | 2316.77 | 0.026459 | 2316.77 | 0.026459 | 2316.77 | 0.026459 | 2316.77 | 0.026459
1978.17 | 0.028236 | 1978.17 | 0.028236 | 1978.17 | 0.028236 | 1978.17 | 0.028236 | 1978.17 | 0.028236 | 1978.17 | 0.028236 | 1978.17 | 0.028236
1658.93 | 0.030496 | 1658.93 | 0.030496 | 1658.93 | 0.030496 | 1658.93 | 0.030496 | 1658.93 | 0.030496 | 1658.93 | 0.030496 | 1658.93 | 0.030496
1391.21 | 0.033102 | 1391.21 | 0.033102 | 1391.21 | 0.033102 | 1391.21 | 0.033102 | 1391.21 | 0.033102 | 1391.21 | 0.033102 | 1391.21 | 0.033102
1225.28 | 0.035114 | 1225.28 | 0.035114 | 1225.28 | 0.035114 | 1225.28 | 0.035114 | 1225.28 | 0.035114 | 1225.28 | 0.035114 | 1225.28 | 0.035114
1036.83 | 0.038652 | 1036.83 | 0.038652 | 1036.83 | 0.038652 | 1036.83 | 0.038652 | 1036.83 | 0.038652 | 1036.83 | 0.038652 | 1036.83 | 0.038652
902.285 | 0.041997 | 902.285 | 0.041997 | 902.285 | 0.041997 | 902.285 | 0.041997 | 902.285 | 0.041997 | 902.285 | 0.041997 | 902.285 | 0.041997
794.673 | 0.04586 | 794.673 | 0.04586 | 794.673 | 0.04586 | 794.673 | 0.04586 | 794.673 | 0.04586 | 794.673 | 0.04586 | 794.673 | 0.04586
699.196 | 0.050481 | 699.196 | 0.050481 | 699.196 | 0.050481 | 699.196 | 0.050481 | 699.196 | 0.050481 | 699.196 | 0.050481 | 699.196 | 0.050481
633.292 | 0.054959 | 633.292 | 0.054959 | 633.292 | 0.054959 | 633.292 | 0.054959 | 633.292 | 0.054959 | 633.292 | 0.054959 | 633.292 | 0.054959
568.46 | 0.060983 | 568.46 | 0.060983 | 568.46 | 0.060983 | 568.46 | 0.060983 | 568.46 | 0.060983 | 568.46 | 0.060983 | 568.46 | 0.060983
521.616 | 0.066993 | 521.616 | 0.066993 | 521.616 | 0.066993 | 521.616 | 0.066993 | 521.616 | 0.066993 | 521.616 | 0.066993 | 521.616 | 0.066993
480.07 | 0.073965 | 480.07 | 0.073965 | 480.07 | 0.073965 | 480.07 | 0.073965 | 480.07 | 0.073965 | 480.07 | 0.073965 | 480.07 | 0.073965
437.874 | 0.082813 | 437.874 | 0.082813 | 437.874 | 0.082813 | 437.874 | 0.082813 | 437.874 | 0.082813 | 437.874 | 0.082813 | 437.874 | 0.082813
397.793 | 0.094405 | 397.793 | 0.094405 | 397.793 | 0.094405 | 397.793 | 0.094405 | 397.793 | 0.094405 | 397.793 | 0.094405 | 397.793 | 0.094405
368.312 | 0.10496 | 368.312 | 0.10496 | 368.312 | 0.10496 | 368.312 | 0.10496 | 368.312 | 0.10496 | 368.312 | 0.10496 | 368.312 | 0.10496
331.269 | 0.12317 | 331.269 | 0.12317 | 331.269 | 0.12317 | 331.269 | 0.12317 | 331.269 | 0.12317 | 331.269 | 0.12317 | 331.269 | 0.12317
299.445 | 0.14382 | 299.445 | 0.14382 | 299.445 | 0.14382 | 299.445 | 0.14382 | 299.445 | 0.14382 | 299.445 | 0.14382 | 299.445 | 0.14382
266.915 | 0.17219 | 266.915 | 0.17219 | 266.915 | 0.17219 | 266.915 | 0.17219 | 266.915 | 0.17219 | 266.915 | 0.17219 | 266.915 | 0.17219
235.787 | 0.21137 | 235.787 | 0.21137 | 235.787 | 0.21137 | 235.787 | 0.21137 | 235.787 | 0.21137 | 235.787 | 0.21137 | 235.787 | 0.21137
205.6 | 0.26816 | 205.6 | 0.26816 | 205.6 | 0.26816 | 205.6 | 0.26816 | 205.6 | 0.26816 | 205.6 | 0.26816 | 205.6 | 0.26816
184.921 | 0.32558 | 184.921 | 0.32558 | 184.921 | 0.32558 | 184.921 | 0.32558 | 184.921 | 0.32558 | 184.921 | 0.32558 | 184.921 | 0.32558
162.216 | 0.41472 | 162.216 | 0.41472 | 162.216 | 0.41472 | 162.216 | 0.41472 | 162.216 | 0.41472 | 162.216 | 0.41472 | 162.216 | 0.41472
144.017 | 0.52248 | 144.017 | 0.52248 | 144.017 | 0.52248 | 144.017 | 0.52248 | 144.017 | 0.52248 | 144.017 | 0.52248 | 144.017 | 0.52248
126.587 | 0.68239 | 126.587 | 0.68239 | 126.587 | 0.68239 | 126.587 | 0.68239 | 126.587 | 0.68239 | 126.587 | 0.68239 | 126.587 | 0.68239
112.385 | 0.87358 | 112.385 | 0.87358 | 112.385 | 0.87358 | 112.385 | 0.87358 | 112.385 | 0.87358 | 112.385 | 0.87358 | 112.385 | 0.87358
100.578 | 1.1105 | 100.578 | 1.1105 | 100.578 | 1.1105 | 100.578 | 1.1105 | 100.9095 | 1.0565 | 100.9095 | 1.0565 | 100.578 | 1.1105
91.0068 | 1.3852 | 91.0068 | 1.3852 | 91.0068 | 1.3852 | 91.0068 | 1.3852 | 78.0046 | 1.8252 | 81.192 | 1.7335 | 90.5154 | 1.4107
83.6745 | 1.7243 | 83.6745 | 1.7243 | 81.192 | 1.7335 | 83.6745 | 1.7243 | 57.9316 | 3.5765 | 67.4155 | 2.7721 | 80.4982 | 1.955
81 | 1.8252 | 77.6284 | 2.1594 | 67.4155 | 2.7721 | 77.6284 | 2.1594 | 54.0877 | 4.2224 | 59.4424 | 3.8749 | 68.9761 | 3.3775
57.9316 | 3.5765 | 72.6704 | 2.6962 | 59.4424 | 3.8749 | 72.6704 | 2.6962 | 51.9644 | 4.654 | 52.1132 | 5.6865 | 65.5144 | 4.2588
54.0877 | 4.2224 | 57.9316 | 3.5765 | 52.1132 | 5.6865 | 68.9761 | 3.3775 | 45.0389 | 6.5804 | 47.0136 | 7.9944 | 63.3036 | 5.2336
48.2397 | 4.9282 | 54.0877 | 4.2224 | 47.0136 | 7.9944 | 65.5144 | 4.2588 | 36.1349 | 11.4008 | 43.2708 | 10.7665 | 57.7661 | 9.9088
39.7122 | 6.5054 | 51.9644 | 4.654 | 39.2604 | 10.6439 | 63.3036 | 5.2336 | 34.4197 | 12.7839 | 39.7122 | 15.8 | 51.9644 | 28.0888
29.4088 | 10.1674 | 42.6563 | 6.2678 | 32.0591 | 14.8357 | 55.8168 | 6.5054 | 32.3203 | 15.3103 | 37.6114 | 22.8573 | 47.1483 | 102.7273
24.9244 | 13.1175 | 34.6172 | 8.6615 | 23.3463 | 25.1217 | 46.2135 | 9.0415 | 30.0036 | 19.4719 | 35.6217 | 49.9354 | 44.6541 | 261.1901
21.122 | 17.0208 | 25.4894 | 14.0906 | 20.3572 | 32.3183 | 37.3075 | 13.3066 | 27.7735 | 26.9854 | 34.4197 | 106.0133 | 44.2725 | 300.5188
17.1957 | 24.1349 | 20.9934 | 19.5837 | 17.7494 | 42.7837 | 28.9331 | 21.2179 | 26.3796 | 36.4469 | 33.2582 | 266.4765
13.7206 | 36.5514 | 16.0498 | 31.5866 | 15.5633 | 58.6173 | 23.3535 | 33.3521 | 24.9841 | 54.8824 | 33.0684 | 300.5188
11.1046 | 55.5144 | 12.9177 | 49.7927 | 13.8025 | 83.5946 | 20.5962 | 45.0459 | 23.2597 | 125.1595
9.0383 | 92.6684 | 12.3073 | 56.1537 | 12.9606 | 105.4082 | 18.6368 | 58.7853 | 22.2828 | 261.1901
8.2242 | 124.445 | 11.2969 | 70.8067 | 11.7586 | 168.5594 | 16.7663 | 84.3155 | 22.1556 | 300.5188
7.5689 | 176.9647 | 10.0187 | 101.8489 | 11.1031 | 271.0927 | 15.8793 | 110.3481
7.0455 | 265.7148 | 9.1685 | 144.8322 | 11.069 | 300.5188 | 14.5308 | 202.4488
7.0038 | 300.5188 | 8.8332 | 182.6255 |  |  | 14.3224 | 264.1979
|  | 8.5584 | 243.1519 |  |  | 14.3603 | 300.5188
|  | 8.5077 | 300.5188