## Minimum Melt
S&C Power Fuses - Type SMU-20 (14.4 through 35 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (14.4 through 35 kV)
"DR" Speed (TCC 175-2) | [9 empty] | "DR" Speed (TCC 175-2)
Minimum Melting Time-Current Characteristic Curves Dated August 29, 2005 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated August 29, 2005
Tolerance in Terms of Current: |  |  | Plus 10% | [6 empty] | Tolerance in Terms of Current: |  |  | Plus 10%
3DR |  | 4DR |  | 5DR |  | 7DR |  | 10DR |  | 15DR |  | 20DR
Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current
0.01 | 894.238 | 0.01 | 894.238 | 0.01 | 894.238 | 0.01 | 894.238 | 0.01 | 894.238 | 0.01 | 894.238 | 0.01 | 894.238
0.011908 | 813.6833 | 0.011908 | 813.6833 | 0.011908 | 813.6833 | 0.011908 | 813.6833 | 0.011908 | 813.6833 | 0.011908 | 813.6833 | 0.011908 | 813.6833
0.0772 | 322.057 | 0.0772 | 322.057 | 0.0772 | 322.057 | 0.0772 | 322.057 | 0.0772 | 322.057 | 0.0772 | 322.057 | 0.0772 | 322.057
0.17405 | 215.776 | 0.17405 | 215.776 | 0.17405 | 215.776 | 0.17405 | 215.776 | 0.17405 | 215.776 | 0.17405 | 215.776 | 0.17405 | 215.776
0.32115 | 159.3359 | 0.32115 | 159.3359 | 0.32115 | 159.3359 | 0.32115 | 159.3359 | 0.32115 | 159.3359 | 0.32115 | 159.3359 | 0.32115 | 159.3359
0.61154 | 117.3226 | 0.61154 | 117.3226 | 0.61154 | 117.3226 | 0.61154 | 117.3226 | 0.61154 | 117.3226 | 0.61154 | 117.3226 | 0.61154 | 117.3226
1.0565 | 91.7359 | 1.0565 | 91.7359 | 1.0565 | 91.7359 | 1.0565 | 91.7359 | 1.0565 | 91.7359 | 1.0565 | 91.7359 | 1.0565 | 91.7359
1.8252 | 70.9132 | 1.8252 | 70.9132 | 1.7335 | 73.8109 | 1.4107 | 82.2867 | 1.8252 | 70.9132 | 1.7335 | 73.8109 | 1.4107 | 82.2867
3.5765 | 52.6651 | 3.5765 | 52.6651 | 2.7721 | 61.2868 | 1.955 | 73.1801 | 3.5765 | 52.6651 | 2.7721 | 61.2868 | 1.955 | 73.1801
4.2224 | 49.1707 | 4.2224 | 49.1707 | 3.8749 | 54.0386 | 3.3775 | 62.7056 | 4.2224 | 49.1707 | 3.8749 | 54.0386 | 3.3775 | 62.7056
4.9282 | 43.8543 | 4.654 | 47.2403 | 5.6865 | 47.3757 | 4.2588 | 59.5585 | 4.654 | 47.2403 | 5.6865 | 47.3757 | 4.2588 | 59.5585
6.5054 | 36.102 | 6.2678 | 38.7785 | 7.9944 | 42.7396 | 5.2336 | 57.5487 | 6.5804 | 40.9445 | 7.9944 | 42.7396 | 5.2336 | 57.5487
10.1674 | 26.7353 | 8.6615 | 31.4701 | 10.6439 | 35.6913 | 6.5054 | 50.7425 | 11.4008 | 32.8499 | 10.7665 | 39.3371 | 9.9088 | 52.5146
13.1175 | 22.4544 | 14.0906 | 23.1722 | 14.8357 | 28.8821 | 9.0415 | 42.0123 | 12.7839 | 31.2906 | 15.8 | 36.102 | 28.0888 | 47.2403
17.0208 | 18.8589 | 19.5837 | 18.913 | 25.1217 | 20.8449 | 13.3066 | 33.6103 | 15.3103 | 29.3821 | 22.8573 | 34.1922 | 102.7273 | 42.8621
24.1349 | 15.2174 | 31.5866 | 14.3302 | 32.3183 | 18.0152 | 21.2179 | 25.8331 | 19.4719 | 27.276 | 49.9354 | 32.3834 | 261.1901 | 40.5946
36.5514 | 12.0356 | 49.7927 | 11.4316 | 42.7837 | 15.5697 | 33.3521 | 20.6668 | 26.9854 | 25.2486 | 106.0133 | 31.2906 | 300.5188 | 40.2477
55.5144 | 9.6562 | 56.1537 | 10.7959 | 58.6173 | 13.5333 | 45.0459 | 18.0668 | 36.4469 | 23.9814 | 266.4765 | 30.2347
92.6684 | 7.7917 | 70.8067 | 9.8234 | 83.5946 | 11.8987 | 58.7853 | 16.2059 | 54.8824 | 22.7128 | 300.5188 | 30.0622
124.445 | 7.0292 | 101.8489 | 8.6368 | 105.4082 | 11.0774 | 84.3155 | 14.4537 | 125.1595 | 21.1452
176.9647 | 6.4143 | 144.8322 | 7.8364 | 168.5594 | 9.9649 | 110.3481 | 13.5721 | 261.1901 | 20.2571
265.7148 | 5.9206 | 182.6255 | 7.4858 | 271.0927 | 9.3304 | 202.4488 | 12.3142 | 300.5188 | 20.1415
300.5188 | 5.8365 | 243.1519 | 7.1919 | 300.5188 | 9.2242 | 264.1979 | 12.0356
|  | 300.5188 | 7.0898 |  |  | 300.5188 | 11.9669