## Parallel Total Clear (All)
S&C Parallel Fault Fiter Electronic Power Fuses | [9 empty] | S&C Parallel Fault Fiter Electronic Power Fuses
Inverse Curve-Type Control Modules (TCC 410-7-2-P) | [9 empty] | Inverse Curve-Type Control Modules (TCC 410-7-2-P)
Total Clearing Time-Current Characteristic Curves Dated September 9, 2002 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated September 9, 2002
Tolerance in Terms of Current: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance in Terms of Current: Curves are plotted to maximum test points. All variations are minus.
400A |  | 500A |  | 600A |  | 700A |  | 800A |  | 1000A |  | 1250A |  | 1500A
Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current
700 | 880 | 700 | 1100 | 700 | 1320 | 700 | 1540 | 700 | 1760 | 700 | 2200 | 700 | 2750 | 700 | 3300
500 | 880 | 500 | 1100 | 500 | 1320 | 500 | 1540 | 500 | 1760 | 500 | 2200 | 500 | 2750 | 500 | 3300
300 | 880 | 300 | 1100 | 300 | 1320 | 300 | 1540 | 300 | 1760 | 300 | 2200 | 300 | 2750 | 300 | 3300
200 | 880 | 200 | 1100 | 200 | 1320 | 200 | 1540 | 200 | 1760 | 200 | 2200 | 200 | 2750 | 200 | 3300
100 | 880 | 100 | 1100 | 100 | 1320 | 100 | 1540 | 100 | 1760 | 100 | 2200 | 100 | 2750 | 100 | 3300
70 | 891 | 70 | 1111 | 70 | 1325.5 | 70 | 1551 | 70 | 1771 | 70 | 2211 | 70 | 2772 | 70 | 3322
50 | 902 | 50 | 1116.5 | 50 | 1331 | 50 | 1562 | 50 | 1782 | 50 | 2222 | 50 | 2794 | 50 | 3333
30 | 907.5 | 30 | 1122 | 30 | 1342 | 30 | 1573 | 30 | 1793 | 30 | 2244 | 30 | 2827 | 30 | 3344
20 | 913 | 20 | 1144 | 20 | 1353 | 20 | 1584 | 20 | 1804 | 20 | 2299 | 20 | 2860 | 20 | 3421
10 | 957 | 10 | 1210 | 10 | 1463 | 10 | 1694 | 10 | 1925 | 10 | 2420 | 10 | 3069 | 10 | 3564
7 | 1001 | 7 | 1276 | 7 | 1551 | 7 | 1771 | 7 | 2002 | 7 | 2596 | 7 | 3190 | 7 | 3762
5 | 1056 | 5 | 1353 | 5 | 1639 | 5 | 1870 | 5 | 2167 | 5 | 2717 | 5 | 3443 | 5 | 3982
3 | 1210 | 3 | 1540 | 3 | 1848 | 3 | 2134 | 3 | 2420 | 3 | 3080 | 3 | 3916 | 3 | 4576
2 | 1386 | 2 | 1716 | 2 | 2112 | 2 | 2431 | 2 | 2827 | 2 | 3520 | 2 | 4400 | 2 | 5060
1 | 1826 | 1 | 2310 | 1 | 2860 | 1 | 3320 | 1 | 3784 | 1 | 4730 | 1 | 5960 | 1 | 6985
0.7 | 2211 | 0.7 | 2840 | 0.7 | 3505 | 0.7 | 4050 | 0.7 | 4675 | 0.7 | 5825 | 0.7 | 7250 | 0.7 | 8470
0.5 | 2775 | 0.5 | 3540 | 0.5 | 4475 | 0.5 | 5025 | 0.5 | 5885 | 0.5 | 7300 | 0.5 | 9275 | 0.5 | 10700
0.3 | 4000 | 0.3 | 5215 | 0.3 | 6625 | 0.3 | 7475 | 0.3 | 9000 | 0.3 | 10950 | 0.3 | 14100 | 0.3 | 17200
0.2 | 5800 | 0.2 | 7700 | 0.2 | 9650 | 0.2 | 11150 | 0.2 | 13750 | 0.2 | 16100 | 0.2 | 22000 | 0.2 | 27000
0.1 | 14000 | 0.1 | 17500 | 0.1 | 21200 | 0.1 | 27000 | 0.1 | 34000 | 0.1 | 40000 | 0.123 | 40000 | 0.148 | 40000
0.07 | 25000 | 0.07 | 32300 | 0.07 | 40000 | 0.0765 | 40000 | 0.09 | 40000
0.055 | 40000 | 0.064 | 40000