## 410_7TC
S&C Fault Fiter Electronic Power Fuses | [9 empty] | S&C Fault Fiter Electronic Power Fuses
Inverse Curve-Type Control Modules (TCC 410-7-2) | [9 empty] | Inverse Curve-Type Control Modules (TCC 410-7-2)
Total Clearing Time-Current Characteristic Curves Dated October 13, 1986 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated October 13, 1986
Tolerance in Terms of current: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance in Terms of current: Curves are plotted to maximum test points. All variations are minus.
Min. Pickup = 400A |  | Min. Pickup = 500A |  | Min. Pickup = 600A |  | Min. Pickup = 700A |  | Min. Pickup = 800A |  | Min. Pickup = 1000A |  | Min. Pickup = 1250A |  | Min. Pickup = 1500A
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
44888 | 0.038923 | 44843.1 | 0.043189 | 44843.1 | 0.045722 | 44888 | 0.049878 | 44888 | 0.054249 | 44932.9 | 0.061166 | 44932.9 | 0.070217 | 44932.9 | 0.078696
43911.2 | 0.039236 | 43692.2 | 0.043711 | 42063.1 | 0.047115 | 43084.8 | 0.050937 | 41811.4 | 0.056576 | 42656.1 | 0.063092 | 44087.2 | 0.071278 | 41561.3 | 0.083228
40212.2 | 0.040471 | 39931.7 | 0.045358 | 38984.7 | 0.048891 | 39376.5 | 0.053228 | 39023.7 | 0.058944 | 40131.8 | 0.065274 | 39180.1 | 0.077369 | 37606.2 | 0.08998
35951.5 | 0.042123 | 35987.4 | 0.047541 | 35310.1 | 0.051295 | 34645.6 | 0.057088 | 35380.8 | 0.062464 | 37493.6 | 0.068074 | 34784.4 | 0.084149 | 34369.5 | 0.096312
31886.1 | 0.04415 | 32497.7 | 0.049829 | 30912.8 | 0.054904 | 30789.4 | 0.060861 | 32497.7 | 0.065864 | 34369.5 | 0.071923 | 30361.3 | 0.092813 | 30974.7 | 0.10444
27554.6 | 0.046833 | 28794.1 | 0.052857 | 27748.2 | 0.058358 | 26580.3 | 0.066326 | 28679.1 | 0.071278 | 31632 | 0.075761 | 26740.3 | 0.10206 | 27859.4 | 0.1137
24268.3 | 0.04953 | 25538.1 | 0.056182 | 24365.5 | 0.062714 | 23457 | 0.071707 | 25975.9 | 0.075989 | 29170.9 | 0.080045 | 22855 | 0.11496 | 23811.5 | 0.12923
21267.3 | 0.052751 | 22068.9 | 0.060618 | 21331.2 | 0.067734 | 20230.1 | 0.078696 | 23293.4 | 0.08158 | 27036 | 0.084402 | 19730.6 | 0.12923 | 20950.7 | 0.14382
18286.6 | 0.056746 | 18068.5 | 0.06787 | 18525.9 | 0.073891 | 17273.4 | 0.087234 | 21246 | 0.086885 | 24982.4 | 0.089442 | 17135.8 | 0.14483 | 18177.2 | 0.16232
15520.6 | 0.061842 | 15350.8 | 0.074783 | 15929.4 | 0.081336 | 14514.8 | 0.098061 | 19436.8 | 0.092258 | 22832.2 | 0.095353 | 15107.2 | 0.16071 | 16154 | 0.17922
13425.7 | 0.066926 | 13199.4 | 0.082154 | 14170.6 | 0.087671 | 12455.6 | 0.10924 | 17482 | 0.099444 | 21076.7 | 0.10115 | 13318.7 | 0.1785 | 14399.1 | 0.19846
11509.5 | 0.073009 | 11718.5 | 0.088729 | 12405.9 | 0.095544 | 10981 | 0.11965 | 15818.3 | 0.10665 | 19456.3 | 0.10751 | 11907.5 | 0.19668 | 12860.6 | 0.21955
10177.4 | 0.078696 | 10126.6 | 0.097085 | 10487.3 | 0.10708 | 9671.4 | 0.13158 | 14413.6 | 0.11427 | 18122.8 | 0.11336 | 10731.3 | 0.21585 | 11544 | 0.24216
8990.54 | 0.084655 | 8768.56 | 0.10665 | 8909.99 | 0.11977 | 8594.93 | 0.14339 | 12719.9 | 0.12554 | 16431 | 0.12207 | 9613.54 | 0.23784 | 10466.4 | 0.26523
8045.98 | 0.090885 | 7981.87 | 0.11382 | 7808.19 | 0.13145 | 7645.92 | 0.15627 | 11555.6 | 0.1345 | 14867.4 | 0.13184 | 8586.34 | 0.26233 | 9329.42 | 0.29548
7150.43 | 0.097963 | 7236.75 | 0.12207 | 6788.11 | 0.14571 | 6863.19 | 0.16895 | 10218.2 | 0.14776 | 13199.4 | 0.14512 | 7661.23 | 0.28992 | 8458.51 | 0.32427
6515.43 | 0.10402 | 6781.33 | 0.12782 | 6050.69 | 0.15911 | 6291.33 | 0.18084 | 9026.57 | 0.16249 | 11871.8 | 0.15768 | 7079.28 | 0.31156 | 7668.9 | 0.35588
5984.5 | 0.11001 | 6234.96 | 0.13613 | 5371.85 | 0.17497 | 5854.28 | 0.1903 | 8216.73 | 0.17479 | 10529.4 | 0.17357 | 6502.41 | 0.33448 | 6925.24 | 0.39252
5602.28 | 0.11542 | 5709.74 | 0.14556 | 4919.33 | 0.18935 | 5409.59 | 0.20389 | 7547.17 | 0.1869 | 9508.37 | 0.18897 | 5948.7 | 0.36489 | 6367.28 | 0.42521
5218.31 | 0.12195 | 5270.75 | 0.15472 | 4433.43 | 0.20947 | 4973.74 | 0.22043 | 7058.08 | 0.1957 | 8733.56 | 0.20247 | 5485.85 | 0.39567 | 5813.44 | 0.46433
4764.41 | 0.13105 | 4924.25 | 0.16412 | 3999.51 | 0.23406 | 4554.76 | 0.24168 | 6574.33 | 0.20677 | 8062.09 | 0.2165 | 5114.98 | 0.42735 | 5524.39 | 0.48667
4433.43 | 0.13971 | 4609.75 | 0.17392 | 3629.78 | 0.26259 | 4137.84 | 0.26924 | 5990.49 | 0.22287 | 7405.13 | 0.2329 | 4778.72 | 0.46479 | 5307.78 | 0.50907
4117.2 | 0.14954 | 4302.4 | 0.1856 | 3261.45 | 0.30205 | 3835.01 | 0.29607 | 5574.33 | 0.23808 | 6822.14 | 0.24879 | 4398.1 | 0.5178 | 4998.68 | 0.55092
3865.82 | 0.15943 | 3936.03 | 0.20287 | 3050.1 | 0.33049 | 3456.21 | 0.33886 | 5207.88 | 0.25407 | 6412.01 | 0.26259 | 4100.76 | 0.57226 | 4702.87 | 0.5986
3655.28 | 0.16861 | 3608.07 | 0.22332 | 2782.01 | 0.37226 | 3004.69 | 0.40732 | 4831.58 | 0.2755 | 5984.5 | 0.27827 | 3710.52 | 0.67088 | 4276.66 | 0.68924
3384.39 | 0.18412 | 3212.9 | 0.25534 | 2497.21 | 0.42992 | 2656.93 | 0.48183 | 4495.93 | 0.29815 | 5463.96 | 0.30417 | 3421.82 | 0.76862 | 4023.58 | 0.76021
3108.6 | 0.20287 | 2841.05 | 0.29785 | 2286.84 | 0.48473 | 2356.49 | 0.57112 | 4179.42 | 0.32525 | 5099.66 | 0.32688 | 3111.71 | 0.91378 | 3721.67 | 0.87533
2821.23 | 0.22692 | 2667.58 | 0.32395 | 2046.59 | 0.566 | 2058.9 | 0.70106 | 3755.32 | 0.37226 | 4745.39 | 0.35481 | 2861 | 1.0777 | 3515.47 | 0.97613
2524.83 | 0.25816 | 2494.71 | 0.35304 | 1855.53 | 0.64975 | 1859.25 | 0.82683 | 3401.35 | 0.42394 | 4415.73 | 0.38706 | 2614.76 | 1.2941 | 3290.94 | 1.1217
2248.3 | 0.29577 | 2279.99 | 0.39449 | 1689.06 | 0.75189 | 1699.23 | 0.96256 | 3074.59 | 0.48619 | 4108.97 | 0.42564 | 2447.76 | 1.5006 | 3080.75 | 1.2902
2004.05 | 0.3392 | 2096.3 | 0.4386 | 1542.14 | 0.87445 | 1578.02 | 1.1017 | 2843.89 | 0.54381 | 3796.85 | 0.47561 | 2326.05 | 1.7021 | 2895.54 | 1.4916
1802.5 | 0.38514 | 1861.11 | 0.51368 | 1442.2 | 0.98495 | 1493.57 | 1.2188 | 2614.76 | 0.61745 | 3543.71 | 0.52458 | 2170.97 | 2.0644 | 2737.85 | 1.7157
1582.76 | 0.45061 | 1747.48 | 0.55869 | 1344.7 | 1.1195 | 1430.71 | 1.3322 | 2472.36 | 0.67357 | 3271.25 | 0.59205 | 2042.5 | 2.4989 | 2542.56 | 2.0893
1490.59 | 0.48425 | 1627.71 | 0.6156 | 1279.12 | 1.2347 | 1375.99 | 1.465 | 2241.56 | 0.78729 | 3016.73 | 0.67425 | 1942.88 | 2.9619 | 2384.94 | 2.5443
1395.39 | 0.52932 | 1498.06 | 0.69756 | 1201.02 | 1.4118 | 1294.56 | 1.6987 | 2079.59 | 0.89033 | 2770.9 | 0.77712 | 1853.68 | 3.5003 | 2261.83 | 3.0037
1303.65 | 0.58265 | 1408 | 0.76479 | 1134.48 | 1.6288 | 1203.42 | 2.0644 | 1954.57 | 0.99088 | 2578.41 | 0.87971 | 1765.04 | 4.2582 | 2147.22 | 3.5961
1220.39 | 0.64072 | 1288.1 | 0.88589 | 1073.77 | 1.8848 | 1124.31 | 2.5114 | 1809.72 | 1.1352 | 2404.09 | 0.99884 | 1694.14 | 5.1082 | 2056.84 | 4.3096
1153.93 | 0.69896 | 1186.69 | 1.019 | 1007.2 | 2.2679 | 1065.21 | 2.9947 | 1712.87 | 1.2672 | 2230.38 | 1.1535 | 1660.59 | 5.6285 | 1978.17 | 5.2166
1080.23 | 0.77402 | 1108.68 | 1.1547 | 954.255 | 2.6774 | 1014.27 | 3.5425 | 1622.83 | 1.4118 | 2098.39 | 1.3071 | 1616.35 | 6.442 | 1908.22 | 6.3525
1004.18 | 0.87009 | 1048.3 | 1.298 | 914.092 | 3.0797 | 980.371 | 3.9743 | 1548.32 | 1.5791 | 1986.1 | 1.4577 | 1571.72 | 7.7357 | 1846.28 | 7.8683
940.048 | 0.97711 | 974.506 | 1.5432 | 882.652 | 3.5284 | 953.301 | 4.4453 | 1474.28 | 1.7751 | 1868.57 | 1.6767 | 1529.85 | 9.2984 | 1804.3 | 9.4673
910.443 | 1.0344 | 915.922 | 1.8055 | 849.74 | 4.0871 | 921.434 | 5.2375 | 1412.23 | 1.9854 | 1770.34 | 1.9384 | 1493.57 | 11.4026 | 1757.99 | 12.2907
869.511 | 1.1341 | 861.72 | 2.1315 | 825.452 | 4.599 | 886.19 | 6.5656 | 1342.01 | 2.2907 | 1670.58 | 2.3021 | 1462.54 | 13.9411 | 1724.91 | 15.6872
829.589 | 1.2584 | 816.422 | 2.4989 | 799.456 | 5.4024 | 861.72 | 7.79 | 1276.56 | 2.6481 | 1592.29 | 2.6801 | 1440.76 | 16.4421 | 1694.14 | 20.8185
789.919 | 1.4089 | 771.959 | 2.9917 | 777.381 | 6.3208 | 842.127 | 9.3077 | 1227.74 | 2.9649 | 1517.66 | 3.1735 | 1413.65 | 21.1332 | 1673.93 | 27.7947
740.948 | 1.6468 | 733.576 | 3.571 | 757.43 | 7.4249 | 822.979 | 11.4942 | 1185.51 | 3.3698 | 1455.24 | 3.7279 | 1398.18 | 26.9194 | 1665.58 | 35.868
702.701 | 1.8886 | 707.637 | 4.0708 | 739.468 | 8.8538 | 809.107 | 13.83 | 1136.75 | 3.9783 | 1396.78 | 4.4676 | 1387.04 | 34.9126 | 1663.91 | 48.7569
667.761 | 2.1833 | 677.176 | 4.859 | 723.377 | 10.7171 | 795.468 | 17.337 | 1091.08 | 4.7486 | 1352.79 | 5.1338 | 1377.36 | 47.2214 | 1667.24 | 64.3829
623.863 | 2.672 | 649.973 | 6.0005 | 709.053 | 13.0377 | 784.409 | 21.6899 | 1052.5 | 5.6341 | 1301.05 | 6.208 | 1370.49 | 65.2906 | 1667.24 | 92.7446
588.12 | 3.2409 | 621.994 | 7.8213 | 696.405 | 15.75 | 775.828 | 28.756 | 1023.44 | 6.5919 | 1267.66 | 7.2344 | 1366.39 | 84.1709 | 1663.91 | 140.731
565.625 | 3.6908 | 606.031 | 9.4863 | 685.351 | 19.8032 | 771.959 | 38.3152 | 995.187 | 7.7434 | 1241.32 | 8.3465 | 1367.76 | 112.263 | 1665.58 | 216.99
551.66 | 4.0749 | 587.532 | 12.377 | 676.499 | 24.4064 | 770.416 | 53.3486 | 975.481 | 8.8538 | 1211.88 | 10.3381 | 1367.76 | 150.633 | 1667.24 | 323.711
534.82 | 4.7391 | 575.898 | 15.5156 | 671.109 | 30.4427 | 770.416 | 71.5824 | 956.165 | 10.3175 | 1189.07 | 12.5014 | 1366.39 | 205.789 | 1667.24 | 479.073
519.533 | 5.5115 | 566.191 | 19.7044 | 667.094 | 37.1085 | 771.187 | 99.4694 | 936.295 | 12.377 | 1170.2 | 14.9819 | 1366.39 | 291.445 | 1667.24 | 685.984
505.188 | 6.4549 | 556.091 | 26.6515 | 664.431 | 47.5056 | 770.416 | 140.449 | 920.513 | 14.7588 | 1155.08 | 17.7937 | 1365.02 | 414.823 | 1667.24 | 927.836
493.702 | 7.5146 | 551.108 | 34.8777 | 664.431 | 62.0443 | 771.187 | 214.187 | 905.902 | 17.7227 | 1140.16 | 21.7986 | 1365.02 | 556.603 | 1667.24 | 994.117
484.894 | 8.6265 | 546.717 | 48.4168 | 664.431 | 84.7622 | 771.187 | 338.611 | 895.096 | 21.1332 | 1128.82 | 28.4983 | 1363.66 | 758.129 | 1667.24 | 1000.1
476.244 | 9.9627 | 546.17 | 71.2966 | 663.767 | 116.378 | 771.959 | 523.142 | 887.964 | 25.4024 | 1119.82 | 37.8203 | 1365.02 | 931.554
468.217 | 11.7734 | 545.625 | 98.4796 | 663.767 | 166.143 | 773.504 | 844.593 | 880.888 | 31.6534 | 1112.01 | 50.696 | 1365.02 | 999.1
461.246 | 13.983 | 546.717 | 158.04 | 665.761 | 231.563 | 773.504 | 1002.1 | 874.744 | 40.0788 | 1109.79 | 68.9133 | 1365.02 | 1000.1
454.833 | 16.5245 | 547.264 | 229.717 | 666.427 | 345.106 |  |  | 868.642 | 51.1544 | 1107.57 | 94.6182
448.959 | 19.5474 | 547.811 | 331.574 | 667.094 | 504.644 |  |  | 866.906 | 63.1712 | 1106.47 | 143.143
444.492 | 23.3792 | 547.811 | 520.013 | 667.094 | 736.459 |  |  | 865.174 | 80.3064 | 1106.47 | 213.973
441.391 | 28.6985 | 548.908 | 790.649 | 667.094 | 924.132 |  |  | 866.906 | 112.376 | 1107.57 | 335.577
438.312 | 36.483 | 548.908 | 1004.1 | 667.094 | 1004.1 |  |  | 866.906 | 156.938 | 1107.57 | 506.666
436.999 | 45.5061 | [6 empty] | 866.906 | 226.977 | 1108.68 | 758.888
436.562 | 60.5124 | [6 empty] | 866.906 | 351.726 | 1110.9 | 934.353
436.562 | 83.7511 | [6 empty] | 867.774 | 552.721 | 1108.68 | 1004.1
436.562 | 119.324 | [6 empty] | 867.774 | 840.38
436.999 | 188.83 | [6 empty] | 867.774 | 1004.1
437.874 | 289.123
437.874 | 436.528
437.874 | 625.064
438.312 | 883.467
438.312 | 1005.11