## 410-7
S&C Fault Fiter Eectronic Power Fuses | [7 empty] | S&C Fault Fiter Eectronic Power Fuses
Inverse Curve-Type Control Modules (TCC 410-7) | [7 empty] | Inverse Curve-Type Control Modules (TCC 410-7)
Minimum Tripping Time-Current Characteristic Curve Dated October 13, 1986 | [7 empty] | Minimum Tripping Time-Current Characteristic Curve Dated October 13, 1986
Tolerance in Terms of Current: Plus 10% | [7 empty] | Tolerance in Terms of Current: Plus 10%
Min. Pickup = 400A |  | Min. Pickup = 500A |  | Min. Pickup = 600A |  | Min. Pickup = 700A |  | Min. Pickup = 800A |  | Min. Pickup = 1000 A |  | Min. Pickup = 1250 A |  | Min. Pickup = 1500 A
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
396.6015 | 1000 | 496.673 | 1000 | 603.6119 | 1000 | 699.8957 | 1000 | 785.1942 | 1000 | 1003.181 | 1000 | 1235.129 | 1000 | 1508.59 | 1000
396.6015 | 883.4675 | 496.673 | 790.6493 | 603.6119 | 924.1317 | 699.8957 | 844.5927 | 785.1942 | 840.3801 | 1005.189 | 934.353 | 1235.129 | 931.5539 | 1508.59 | 927.8354
396.2051 | 625.0639 | 495.6807 | 520.0125 | 603.6119 | 736.4589 | 698.4974 | 523.1423 | 785.1942 | 552.7206 | 1003.181 | 758.8879 | 1233.895 | 758.1291 | 1508.59 | 685.9833
396.2051 | 436.5281 | 495.6807 | 331.5744 | 603.6119 | 504.644 | 697.7993 | 338.611 | 784.4094 | 351.7259 | 1002.178 | 506.6664 | 1235.129 | 556.6038 | 1508.59 | 479.0731
396.2051 | 289.123 | 495.1851 | 229.7178 | 603.0087 | 345.1062 | 697.7993 | 214.1873 | 784.4094 | 226.9776 | 1002.178 | 335.5773 | 1235.129 | 414.8235 | 1508.59 | 323.7113
395.4135 | 188.8306 | 494.6902 | 158.0405 | 602.406 | 231.5628 | 697.1019 | 140.4498 | 784.4094 | 156.9379 | 1001.177 | 213.9733 | 1236.365 | 291.445 | 1507.082 | 216.99
395.0183 | 119.3249 | 493.7018 | 98.4796 | 600.6014 | 166.1432 | 697.7993 | 99.4694 | 784.4094 | 112.3759 | 1001.177 | 143.1438 | 1236.365 | 205.7889 | 1505.576 | 140.7309
395.0183 | 83.7511 | 494.1958 | 71.2966 | 600.6014 | 116.3788 | 697.1019 | 71.5824 | 782.8423 | 80.3064 | 1002.178 | 94.6182 | 1237.601 | 150.6336 | 1508.59 | 92.7446
395.0183 | 60.5124 | 494.6902 | 48.4168 | 601.2022 | 84.7621 | 697.1019 | 53.3486 | 784.4094 | 63.1712 | 1004.184 | 68.9133 | 1237.601 | 112.2636 | 1508.59 | 64.3829
395.4135 | 45.5062 | 498.6638 | 34.8428 | 601.2022 | 62.0443 | 698.4974 | 38.3152 | 785.9801 | 51.1544 | 1006.195 | 50.696 | 1236.365 | 84.1709 | 1505.576 | 48.7569
396.6015 | 36.4466 | 503.1719 | 26.6249 | 601.2022 | 47.5056 | 701.9987 | 28.7273 | 791.5012 | 40.0788 | 1013.263 | 37.8204 | 1240.08 | 65.2906 | 1507.082 | 35.8322
399.3874 | 28.6699 | 512.311 | 19.6848 | 603.6119 | 37.1086 | 709.7631 | 21.6682 | 797.0612 | 31.6218 | 1021.402 | 28.4699 | 1246.295 | 47.2214 | 1514.636 | 27.767
402.1929 | 23.3558 | 521.0947 | 15.5001 | 607.2446 | 30.4123 | 719.7696 | 17.3197 | 803.4631 | 25.3771 | 1031.667 | 21.7768 | 1255.05 | 34.8777 | 1532.921 | 20.7978
406.2351 | 19.5279 | 531.6215 | 12.3647 | 612.1219 | 24.382 | 732.1104 | 13.8163 | 809.9166 | 21.1121 | 1045.166 | 17.7759 | 1265.131 | 26.8925 | 1560.763 | 15.6715
411.5507 | 16.508 | 548.3599 | 9.4673 | 620.1315 | 19.7835 | 744.6625 | 11.4713 | 819.6942 | 17.705 | 1058.842 | 14.967 | 1279.124 | 21.1121 | 1590.702 | 12.2784
417.3528 | 13.9691 | 562.8042 | 7.8056 | 630.1332 | 15.7343 | 761.9884 | 9.2891 | 832.9146 | 14.7441 | 1075.919 | 12.489 | 1303.659 | 16.4257 | 1632.602 | 9.4484
423.6603 | 11.7499 | 588.1203 | 5.9825 | 641.5784 | 13.0247 | 779.717 | 7.7745 | 847.1953 | 12.3647 | 1096.557 | 10.3175 | 1323.362 | 13.9272 | 1670.587 | 7.8526
430.9242 | 9.9428 | 612.7343 | 4.8397 | 654.5391 | 10.6957 | 801.8579 | 6.5459 | 865.1745 | 10.2969 | 1123.193 | 8.3298 | 1351.447 | 11.3799 | 1726.636 | 6.3334
438.7509 | 8.6093 | 640.2966 | 4.0505 | 669.0984 | 8.8361 | 833.7479 | 5.2166 | 882.6522 | 8.8361 | 1147.029 | 7.2127 | 1384.273 | 9.2798 | 1789.928 | 5.1958
446.7199 | 7.4996 | 663.7671 | 3.5532 | 685.3512 | 7.4101 | 862.5826 | 4.4275 | 900.4828 | 7.728 | 1177.243 | 6.1894 | 1422.158 | 7.7202 | 1861.114 | 4.2924
457.1135 | 6.4356 | 698.4974 | 2.9738 | 703.404 | 6.3019 | 887.0765 | 3.9545 | 926.0526 | 6.5722 | 1224.063 | 5.1133 | 1462.541 | 6.4227 | 1942.887 | 3.5781
470.0937 | 5.495 | 738.7291 | 2.4814 | 723.3776 | 5.3862 | 917.7557 | 3.5249 | 952.3484 | 5.6173 | 1263.866 | 4.4497 | 1502.567 | 5.6116 | 2046.59 | 2.9857
483.9259 | 4.7202 | 779.717 | 2.1124 | 746.9 | 4.5807 | 963.8455 | 2.9768 | 987.2578 | 4.7296 | 1316.762 | 3.7093 | 1532.921 | 5.0878 | 2157.985 | 2.5265
499.1626 | 4.0546 | 828.7603 | 1.7875 | 768.8771 | 4.0708 | 1017.324 | 2.4939 | 1028.576 | 3.9584 | 1373.243 | 3.1545 | 1597.077 | 4.2412 | 2300.611 | 2.0706
511.7988 | 3.6724 | 881.77 | 1.5248 | 798.6567 | 3.5108 | 1088.908 | 2.0459 | 1072.697 | 3.353 | 1440.766 | 2.6614 | 1677.283 | 3.4828 | 2477.313 | 1.697
532.1533 | 3.2215 | 948.5469 | 1.28 | 827.1046 | 3.0613 | 1171.372 | 1.6801 | 1110.906 | 2.9472 | 1511.61 | 2.2838 | 1757.997 | 2.9442 | 2620 | 1.4738
564.4951 | 2.6534 | 1003.181 | 1.1364 | 863.446 | 2.6587 | 1245.049 | 1.4461 | 1155.087 | 2.6296 | 1601.875 | 1.921 | 1848.131 | 2.4814 | 2787.582 | 1.2723
604.2158 | 2.1659 | 1073.77 | 1.0008 | 911.3538 | 2.2498 | 1294.566 | 1.3137 | 1214.31 | 2.2724 | 1690.755 | 1.6584 | 1964.376 | 2.0459 | 2977.769 | 1.1039
635.8302 | 1.8698 | 1165.529 | 0.86748 | 971.5871 | 1.8661 | 1351.447 | 1.2006 | 1277.845 | 1.9677 | 1797.101 | 1.4388 | 2104.704 | 1.6834 | 3180.932 | 0.95776
670.4382 | 1.6288 | 1274.018 | 0.74665 | 1026.521 | 1.611 | 1427.858 | 1.0831 | 1333.991 | 1.7574 | 1898.71 | 1.289 | 2214.828 | 1.4827 | 3367.512 | 0.85713
714.7488 | 1.3907 | 1355.507 | 0.67898 | 1086.733 | 1.3935 | 1537.527 | 0.94444 | 1400.985 | 1.5602 | 2018.137 | 1.1352 | 2365.938 | 1.2761 | 3640.693 | 0.74218
750.644 | 1.2397 | 1472.814 | 0.5974 | 1157.399 | 1.2163 | 1682.322 | 0.80883 | 1468.403 | 1.3935 | 2175.318 | 0.98004 | 2588.748 | 1.0595 | 3869.689 | 0.67088
786.7664 | 1.1161 | 1581.186 | 0.54055 | 1216.74 | 1.1017 | 1862.975 | 0.68307 | 1549.876 | 1.2484 | 2333.046 | 0.86143 | 2815.598 | 0.89569 | 4255.337 | 0.58033
823.803 | 1.016 | 1684.005 | 0.49551 | 1304.964 | 0.96642 | 2132.243 | 0.55258 | 1637.507 | 1.1172 | 2507.22 | 0.75869 | 3096.196 | 0.75039 | 4522.992 | 0.53251
850.5906 | 0.95872 | 1896.812 | 0.42014 | 1395.392 | 0.85628 | 2404.097 | 0.4634 | 1768.577 | 0.97223 | 2729.653 | 0.65563 | 3357.425 | 0.65236 | 4802.678 | 0.49058
908.6237 | 0.85201 | 2063.028 | 0.376 | 1528.329 | 0.73333 | 2718.756 | 0.38901 | 1881.699 | 0.87183 | 2959.956 | 0.57398 | 3710.528 | 0.55424 | 4998.679 | 0.46853
977.4341 | 0.75566 | 2257.312 | 0.33482 | 1678.961 | 0.63118 | 3127.313 | 0.32073 | 2028.253 | 0.76862 | 3206.481 | 0.50654 | 3979.571 | 0.49949 | 5260.224 | 0.44612
1044.121 | 0.68034 | 2413.734 | 0.3057 | 1851.831 | 0.54763 | 3470.068 | 0.27771 | 2237.087 | 0.65497 | 3435.54 | 0.45742 | 4323.97 | 0.44657 | 5761.361 | 0.40691
1104.26 | 0.62241 | 2570.69 | 0.27966 | 2069.226 | 0.46666 | 3744.073 | 0.25103 | 2365.938 | 0.5992 | 3717.957 | 0.40732 | 4628.227 | 0.40895 | 6266.222 | 0.37413
1179.6 | 0.5643 | 2907.153 | 0.23713 | 2259.571 | 0.41141 | 4121.321 | 0.22332 | 2573.263 | 0.52563 | 3995.521 | 0.36892 | 4963.811 | 0.37751 | 6939.108 | 0.33751
1262.603 | 0.51111 | 3264.721 | 0.20491 | 2517.269 | 0.3541 | 4500.435 | 0.20207 | 2782.012 | 0.46806 | 4293.808 | 0.3365 | 5382.611 | 0.34675 | 7653.579 | 0.306
1348.746 | 0.46572 | 3561.473 | 0.18449 | 2759.845 | 0.31218 | 4894.802 | 0.1856 | 3077.675 | 0.40569 | 4614.363 | 0.30846 | 5883.628 | 0.31627 | 8441.611 | 0.27716
1432.148 | 0.4325 | 3892.976 | 0.16727 | 2951.09 | 0.28389 | 5297.176 | 0.17202 | 3397.957 | 0.3541 | 4943.996 | 0.28589 | 6405.605 | 0.29312 | 9470.417 | 0.24705
1630.971 | 0.36672 | 4171.076 | 0.15565 | 3284.368 | 0.24435 | 5692.637 | 0.16249 | 3781.702 | 0.30692 | 5415.004 | 0.25998 | 6932.173 | 0.27167 | 10445.52 | 0.22376
1813.349 | 0.32105 | 4455.654 | 0.14585 | 3618.915 | 0.21585 | 6210.078 | 0.15059 | 4068.092 | 0.27994 | 5801.832 | 0.24435 | 7769.247 | 0.2441 | 11636.8 | 0.20126
2034.347 | 0.27744 | 4769.177 | 0.1364 | 4011.535 | 0.19125 | 6918.322 | 0.13791 | 4371.796 | 0.25713 | 6172.929 | 0.23058 | 8698.696 | 0.21955 | 13028.94 | 0.18011
2284.563 | 0.23999 | 5166.388 | 0.12731 | 4451.201 | 0.17099 | 7777.02 | 0.12516 | 4712.29 | 0.23571 | 6700.442 | 0.21456 | 9710.163 | 0.19747 | 14616.81 | 0.16087
2552.758 | 0.20864 | 5641.633 | 0.11787 | 4860.658 | 0.15674 | 8751.046 | 0.11325 | 5043.871 | 0.21977 | 7294.884 | 0.19826 | 10774.4 | 0.17832 | 16447.48 | 0.14397
2812.783 | 0.18467 | 6136.002 | 0.10957 | 5474.897 | 0.14084 | 9936.085 | 0.10135 | 5420.421 | 0.2045 | 7902.453 | 0.18412 | 12051.3 | 0.16023 | 18956.98 | 0.12554
3062.325 | 0.16577 | 6548.09 | 0.10371 | 6142.142 | 0.12743 | 11270.32 | 0.090975 | 5948.705 | 0.1884 | 8603.535 | 0.17065 | 13669.58 | 0.14239 | 21545.61 | 0.1109
3307.439 | 0.15029 | 7222.298 | 0.095544 | 7065.144 | 0.11314 | 13133.58 | 0.079726 | 6386.417 | 0.17743 | 9527.411 | 0.15534 | 15505.15 | 0.12654 | 25208.26 | 0.095449
3497.939 | 0.14112 | 7934.125 | 0.088375 | 8062.093 | 0.10145 | 15629.69 | 0.068895 | 6828.966 | 0.16861 | 10742.12 | 0.13943 | 17853.01 | 0.1109 | 28027.09 | 0.086107
3725.399 | 0.13131 | 9162.993 | 0.078775 | 9489.378 | 0.088818 | 18304.96 | 0.060376 | 7434.812 | 0.15643 | 11943.33 | 0.1268 | 20680.11 | 0.096698 | 31098.88 | 0.077991
4011.535 | 0.12146 | 10603.38 | 0.070428 | 11225.33 | 0.077292 | 21224.84 | 0.053442 | 8167.584 | 0.14426 | 13452.6 | 0.11348 | 24195.63 | 0.083813 | 34027.58 | 0.071635
4311.018 | 0.1128 | 11943.33 | 0.063853 | 12822.13 | 0.069379 | 24050.89 | 0.048019 | 9245.833 | 0.12949 | 14867.42 | 0.10381 | 27472.12 | 0.074559 | 37606.29 | 0.064948
4721.723 | 0.10361 | 13890.05 | 0.05652 | 14413.6 | 0.063029 | 27859.44 | 0.042589 | 10455.97 | 0.11623 | 16398.21 | 0.095068 | 31474.31 | 0.065864 | 40697.69 | 0.060315
5069.152 | 0.097085 | 16349.09 | 0.04958 | 16762.97 | 0.055567 | 31348.66 | 0.038768 | 11509.5 | 0.10719 | 17604.81 | 0.089263 | 35451.71 | 0.059062 | 42698.82 | 0.057604
5415.004 | 0.091706 | 19968.82 | 0.042334 | 19301.29 | 0.049432 | 35629.41 | 0.034938 | 13041.97 | 0.096023 | 19071.06 | 0.082896 | 39891.82 | 0.052963
5895.408 | 0.085677 | 23107.84 | 0.037886 | 22046.9 | 0.044415 | 38984.78 | 0.032642 | 14313.06 | 0.088375 | 20659.43 | 0.07706 | 42698.82 | 0.049432
6469.982 | 0.079646 | 26054.01 | 0.034556 | 25107.63 | 0.040068 | 42656.14 | 0.030404 | 15818.38 | 0.081174 | 22605.02 | 0.071136
7280.31 | 0.072573 | 29405.2 | 0.031519 | 27971.1 | 0.036583 |  |  | 17587.22 | 0.073965 | 24463.25 | 0.066128
8134.979 | 0.066393 | 32562.83 | 0.029241 | 31949.98 | 0.033003 |  |  | 19224.24 | 0.068552 | 26394.92 | 0.061781
9208.925 | 0.060376 | 36131.73 | 0.027047 | 35274.89 | 0.030587 |  |  | 21076.78 | 0.063281 | 28621.89 | 0.057431
10414.23 | 0.05474 | 39534.4 | 0.025396 | 38060.29 | 0.028835 |  |  | 23504.03 | 0.057661 | 31098.88 | 0.053602
12148.1 | 0.048598 | 42613.5 | 0.023989 | 42613.5 | 0.026432 |  |  | 25950 | 0.052963 | 33925.66 | 0.049779
14043.68 | 0.043536 | [6 empty] | 29405.2 | 0.047541 | 36312.84 | 0.046974
16546.46 | 0.038459 | [6 empty] | 32013.94 | 0.044194 | 38596.88 | 0.044772
19243.48 | 0.034453 | [6 empty] | 35310.18 | 0.040633 | 40860.8 | 0.042631
21958.89 | 0.031237 | [6 empty] | 37832.61 | 0.038267 | 42698.82 | 0.041165
24932.49 | 0.028548 | [6 empty] | 40616.37 | 0.035895
28851.78 | 0.025857 | [6 empty] | 42656.14 | 0.034487
32530.28 | 0.023821
36385.54 | 0.022189
39732.57 | 0.020938
42656.14 | 0.019977